## Instrument
REV | ISA | AREA No. | LOOP | ID # | P&ID DWG. # | DESCRIPTION |  |  |  | PANEL | I/O | UNITS | RESPONSIBILITY |  |  | OBSERVATIONS | GEM NOTES:
[6 empty] | Sub Area | Device | Device Type | SPECIFICATION |  |  |  | SUPPLIED BY | MOUNTED BY | WIRED BY
| FIT | 4705A |  | FIT-4705A | PMP-F-47-50-01 | Fryer | Flow Meter Make-up & Fill | Flow Transmitter 3" |  |  |  |  | TBD | TBD | Elec. Contractor
| LIT | 4705A |  | LIT-4705A | PMP-F-47-50-01 | Fryer Kettle Oil Level A | Fryer Tank Level | Level Transmitter | VEGAPULS 64PS64.CEGGIJHXWNAXX |  |  |  | GEM | GEM | Elec. Contractor
| LSH | 4705A |  | LSH-4705A | PMP-F-47-50-01 | Fryer Kettle Oil Level A | High Level | Level Switch | ENDRESS & HAUSER, LIQUIPHANT LEVEL SWITCH, MODEL #FTL71-UGM2BB4E6AL,PROBE LENGTH = 6", PROCESS CONNECTION = NPT 3/4", 316 S.S. W/ HOUSING TAG |  |  |  | GEM | GEM | Elec. Contractor
| SV | 4705A |  | SV-4705A | PMP-F-47-50-01 | Fryer | Solenoid Valve - Waterseal Water 1/2"NPT | Solenoid | ASCO VALVE, 1/2"-NPT, P/N #8210G087 |  |  |  | GEM | GEM | Elec. Contractor
| TE | 4705A |  | TE-4705A | PMP-F-47-50-01 | Fryer A | Oil Outlet #1 Temperature | Temperature Transmitter | E+H,MODEL #TH13-2B12E1B531AK , 4.5" IMMERSION W/3" LAG, 3 WIRE, 316SS HOUSING, TERMINAL BLOCK. |  |  |  | GEM | GEM | Elec. Contractor
| FV | 4705A |  | FV-4705A | PMP-F-47-50-01 | Fryer A | Inlet #1 Flow | Flow Valve 8" | VAC Model D400-D-N-D2-H-4/20-SStag |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4705A |  | XV-4705A | PMP-F-47-50-01 | Fryer A | Ball Valve - Stage A Rapid Fill | Solenoid | 3" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, Axiom AN Valve Controller, ASi Communication with Extended Addressing, SS tubing & fittings, SS TAG |  |  |  | GEM | GEM | Elec. Contractor
| TE | 4705B |  | TE-4705B | PMP-F-47-50-01 | Fryer A | Oil Outlet #2 Temperature | Temperature Transmitter | E+H,MODEL #TH13-2B12E1B531AK , 4.5" IMMERSION W/3" LAG, 3 WIRE, 316SS HOUSING, TERMINAL BLOCK. |  |  |  | GEM | GEM | Elec. Contractor
| FV | 4705B |  | FV-4705B | PMP-F-47-50-01 | Fryer A | Inlet #2 Flow | Flow Valve 6" | VAC Model D400-D-N-D2-H-4/20-SStag |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4705B |  | XV-4705B | PMP-F-47-50-01 | Track A lube | Ball Valve - Track A Lube | Solenoid | 1" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, |  |  |  | GEM | GEM | Elec. Contractor
| TE | 4705C |  | TE-4705C | PMP-F-47-50-01 | Fryer A | Oil Outlet #3 Temperature | Temperature Transmitter | E+H,MODEL #TH13-2B12E1B531AK , 4.5" IMMERSION W/3" LAG, 3 WIRE, 316SS HOUSING, TERMINAL BLOCK. |  |  |  | GEM | GEM | Elec. Contractor
| FV | 4705C |  | FV-4705C | PMP-F-47-50-01 | Fryer A | Inlet #3 Flow | Flow Valve 6" | VAC Model D400-D-N-D2-H-4/20-SStag |  |  |  | GEM | GEM | Elec. Contractor
| FV | 4705D |  | FV-4705D | PMP-F-47-50-01 | Fryer A | Outlet #1 Flow | Flow Gate | VAC Model D400-D-N-D2-H-4/20-SStag |  |  |  | GEM | GEM | Elec. Contractor
| FV | 4705E |  | FV-4705E | PMP-F-47-50-01 | Fryer A | Outlet #2 Flow | Flow Gate | VAC Model D400-D-N-D2-H-4/20-SStag |  |  |  | GEM | GEM | Elec. Contractor
| FV | 4705F |  | FV-4705F | PMP-F-47-50-01 | Fryer A | Outlet #3 Flow | Flow Gate | VAC Model D400-D-N-D2-H-4/20-SStag |  |  |  | GEM | GEM | Elec. Contractor
| ZSD | 4706A |  | ZSD-4706A | PMP-F-47-50-01 | Hood A | Infeed Baffle Position DN | Position Transmitter | PROXIMITY SUITCHES, #871TM-BH8N18-N3 MINI-CHANGE STYLE, AC/DC 20-240 VAC, ALLEN-BRADLEY |  |  |  | GEM | GEM | Elec. Contractor
| ZSU | 4706A |  | ZSU-4706A | PMP-F-47-50-01 | Hood | Infeed Baffle Position UP | Proximity Switch | PROXIMITY SUITCHES, #871TM-BH8N18-N3 MINI-CHANGE STYLE, AC/DC 20-240 VAC, ALLEN-BRADLEY |  |  |  | GEM | GEM | Elec. Contractor
| HSD | 4706A |  | HSD-4706A | PMP-F-47-50-01 | Hood A | Lower Baffle Button | Hand Switch | DISCRETE |  |  |  | OTHERS | Mech. Contractor | Elec. Contractor
| HSU | 4706B |  | HSU-4706B | PMP-F-47-50-01 | Hood A | Raise Baffle Button | Hand Switch | DISCRETE |  |  |  | OTHERS | Mech. Contractor | Elec. Contractor
| SS | 4707A |  | SS-4707A | PMP-F-47-50-01 | Hood | Jack Shaft Rotaion Detction Equipment side | Proximity Switch | PROXIMITY SUITCHES, #871TM-BH8N18-N3 MINI-CHANGE STYLE, AC/DC 20-240 VAC, ALLEN-BRADLEY |  |  |  | GEM | GEM | Elec. Contractor
| SS | 4707B |  | SS-4707B | PMP-F-47-50-01 | Hood | Jack Shaft Rotaion Detction Equipment far side | Proximity Switch | PROXIMITY SUITCHES, #871TM-BH8N18-N3 MINI-CHANGE STYLE, AC/DC 20-240 VAC, ALLEN-BRADLEY |  |  |  | GEM | GEM | Elec. Contractor
| HSD | 4707A |  | HSD-4707A | PMP-F-47-50-01 | Hood | HOOD DOWN PUSH BUTTON | Hand Switch | DISCRETE |  |  |  | OTHERS | Mech. Contractor | Elec. Contractor
| ZSU | 4707A |  | ZSU-4707A | PMP-F-47-50-01 | Hood | Hood Position UP | Position Transmitter | IMF ENCODER RV3110 |  |  |  | GEM | GEM | Elec. Contractor
| HSU | 4707B |  | HSU-4707B | PMP-F-47-50-01 | Hood | HOOD LIFT PUSH BUTTON | Hand Switch | DISCRETE |  |  |  | OTHERS | Mech. Contractor | Elec. Contractor
| ZSD | 4707B |  | ZSD-4707B | PMP-F-47-50-01 | Hood | Hood Position DN | Position Transmitter | IMF ENCODER RV3110 |  |  |  | GEM | GEM | Elec. Contractor
| LIT | 4710A |  | LIT-4710A | PMP-F-47-50-01 | Fryer Kettle Oil Level B | Fryer Tank Level - (Bubbler) | Level Transmitter | VEGAPULS 64PS64.CEGGIJHXWNAXX |  |  |  | GEM | GEM | Elec. Contractor
| LSH | 4710A |  | LSH-4710A | PMP-F-47-50-01 | Fryer Kettle Oil Level B | High Level | Level Switch | ENDRESS & HAUSER, LIQUIPHANT LEVEL SWITCH, MODEL #FTL71-UGM2BB4E6AL,PROBE LENGTH = 6", PROCESS CONNECTION = NPT 3/4", 316 S.S. W/ HOUSING TAG |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4710A |  | XV-4710A | PMP-F-47-50-01 | Fryer B | Ball Valve - Stage B Rapid Fill | Solenoid | 3" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, Axiom AN Valve Controller, ASi Communication with Extended Addressing, SS tubing & fittings, SS TAG |  |  |  | GEM | GEM | Elec. Contractor
| TE | 4710A |  | TE-4710A | PMP-F-47-50-01 | Fryer B | Oil Outlet #1 Temperature | Temperature Transmitter | E+H,MODEL #TH13-2B12E1B531AK , 4.5" IMMERSION W/3" LAG, 3 WIRE, 316SS HOUSING, TERMINAL BLOCK. |  |  |  | GEM | GEM | Elec. Contractor
| FV | 4710A |  | FV-4710A | PMP-F-47-50-01 | Fryer B | Inlet #1 Flow | Flow Valve 8" | VAC Model D400-D-N-D2-H-4/20-SStag |  |  |  | GEM | GEM | Elec. Contractor
| TE | 4710B |  | TE-4710B | PMP-F-47-50-01 | Fryer B | Oil Outlet #2 Temperature | Temperature Transmitter | E+H,MODEL #TH13-2B12E1B531AK , 4.5" IMMERSION W/3" LAG, 3 WIRE, 316SS HOUSING, TERMINAL BLOCK. |  |  |  | GEM | GEM | Elec. Contractor
| FV | 4710B |  | FV-4710B | PMP-F-47-50-01 | Fryer B | Inlet #2 Flow | Flow Valve 6" | VAC Model D400-D-N-D2-H-4/20-SStag |  |  |  | GEM | GEM | Elec. Contractor
| TE | 4710C |  | TE-4710C | PMP-F-47-50-01 | Fryer B | Oil Outlet #3 Temperature | Temperature Transmitter | E+H,MODEL #TH13-2B12E1B531AK , 4.5" IMMERSION W/3" LAG, 3 WIRE, 316SS HOUSING, TERMINAL BLOCK. |  |  |  | GEM | GEM | Elec. Contractor
| FV | 4710C |  | FV-4710C | PMP-F-47-50-01 | Fryer B | Inlet #3 Flow | Flow Valve 6" | VAC Model D400-D-N-D2-H-4/20-SStag |  |  |  | GEM | GEM | Elec. Contractor
| TE | 4710D |  | TE-4710D | PMP-F-47-50-01 | Fryer B | Oil Outlet #4 Temperature | Temperature Transmitter | E+H,MODEL #TH13-2B12E1B531AK , 4.5" IMMERSION W/3" LAG, 3 WIRE, 316SS HOUSING, TERMINAL BLOCK. |  |  |  | GEM | GEM | Elec. Contractor
| FV | 4710D |  | FV-4710D | PMP-F-47-50-01 | Fryer B | Inlet #4 Flow | Flow Valve 6" | VAC Model D400-D-N-D2-H-4/20-SStag |  |  |  | GEM | GEM | Elec. Contractor
| FV | 4710E |  | FV-4710E | PMP-F-47-50-01 | Fryer B | Outlet #1 Flow | Flow Gate | VAC Model D400-D-N-D2-H-4/20-SStag |  |  |  | GEM | GEM | Elec. Contractor
| FV | 4710F |  | FV-4710F | PMP-F-47-50-01 | Fryer B | Outlet #2 Flow | Flow Gate | VAC Model D400-D-N-D2-H-4/20-SStag |  |  |  | GEM | GEM | Elec. Contractor
| FV | 4710G |  | FV-4710G | PMP-F-47-50-01 | Fryer B | Outlet #3 Flow | Flow Gate | VAC Model D400-D-N-D2-H-4/20-SStag |  |  |  | GEM | GEM | Elec. Contractor
| FV | 4710H |  | FV-4710H | PMP-F-47-50-01 | Fryer B | Outlet #4 Flow | Flow Gate | VAC Model D400-D-N-D2-H-4/20-SStag |  |  |  | GEM | GEM | Elec. Contractor
| LIT | 4711A |  | LIT-4711A | PMP-F-47-50-01 | Fryer Drip Pan | Purge Tank A | Pressure Transmitter | FMD77-UB37D41DQVAG |  |  |  | GEM | GEM | Elec. Contractor
| LSH | 4711A |  | LSH-4711A | PMP-F-47-50-01 | Fryer Drip Pan | High Level | Level Switch | ENDRESS & HAUSER, LIQUIPHANT LEVEL SWITCH, MODEL #FTL71-UGM2CB4E6AL,PROBE LENGTH = 6", PROCESS CONNECTION = NPT 3/4", 316 S.S. W/ HOUSING TAG |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4711A |  | XV-4711A | PMP-F-47-50-01 | Fryer A/B | Ball Valve - Drip-Pan Drain | Solenoid | 2" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, Axiom AN Valve Controller, ASi Communication with Extended Addressing, SS tubing & fittings, SS TAG |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4714A |  | XV-4714A | PMP-F-47-50-01 | Fryer A/B | Ball Valve - Drip-Pan Oil Pump Drain | Solenoid | 2" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, Axiom AN Valve Controller, ASi Communication with Extended Addressing, SS tubing & fittings, SS TAG |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4713A |  | XV-4713A | PMP-F-47-50-01 | Fryer A/B | Ball Valve - Drip-Pan CIP Pump Drain | Solenoid | 2" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, Axiom AN Valve Controller, ASi Communication with Extended Addressing, SS tubing & fittings, SS TAG |  |  |  | GEM | GEM | Elec. Contractor
| LCV | 4715A |  | LCV-4715A | PMP-F-47-50-02 | Fryer A | Oil Make Up Valve B to A | Control Valve 3" | 3" Fisher Control Valve, Fisher V300 Rotary Valve, 3" V300 2052 Size 2 DVC6200f 317ss Body, HD Seal, Stainless Steel Body, Flanged 300# ANSI Rated, Ball Seal = HD Metal / Packing = Graphite, Modified Equal Percent / Class IV Shut-off, Rotary Actuator = 2052-2507-201319, Left Hand Mounting, Fail close Actuator / DVC6200 4-20HART , Designed to handle 400 F Hot Cooking Oil |  |  |  | GEM | GEM | Elec. Contractor
| ZS | 4715A |  | ZS-4715A | PMP-F-47-50-02 | CONNECTION TANK | CIP Disconnect | Saftey Switch | Allen-Bradley Magnetically CodedMC2 , 2 N.C. Solid-State Relay Safety Outputs 1 x PNP (0.2 A max), Status: OFF (0V DC) Aux Outputs ,, LED Indicator,6 inch Pigtail with 8-Pin Micro (M12) Connector PRT# 440N-Z21W1PH |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4717A |  | XV-4717A | PMP-F-47-50-02 | Fryer A | Ball Valve - Filter #1 Drain | Solenoid | 2" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, Axiom AN Valve Controller, ASi Communication with Extended Addressing, SS tubing & fittings, SS TAG |  |  |  | GEM | GEM | Elec. Contractor
| FS | 4718A |  | FS-4718A | PMP-F-47-50-02 | Circ Pump Stage A | Water Flush Flowmeter | FLOWMETER SWITCH | 1/2" NPT FLOW SWITCH, "FLOTECT", V6EPS-S-S-1-S-MT SERIES V6 FLOW SWITCH, EP = EXPLOSION PROOF, S = STAINLESS STEEL UPPER BODY, S = STAINLESS STEEL LOWER BODY, S = SPDT CIRCUIT (SWITCH), 1 = 1/2" NPT (TEE CONNECTION SIZE), S = STAINLESS STEEL TEE, MT = HIGH TEMPERATURE OPTION RATED FOR 400° F |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4718 |  | XV-4718 | PMP-F-47-50-02 | Fryer A | Steam Quench | Solenoid | 1/2" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, Axiom AN Valve Controller, ASi Communication with Extended Addressing, SS tubing & fittings, SS TAG |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4718A |  | XV-4718A | PMP-F-47-50-02 | Fryer A | Ball Valve - Pump #1 Volute Drain | Solenoid | 3/4" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, Axiom AN Valve Controller, ASi Communication with Extended Addressing, SS tubing & fittings, SS TAG |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4718B |  | XV-4718B | PMP-F-47-50-02 | Fryer A | Ball Valve - Main LP Drain Pump | Solenoid | 4" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, Axiom AN Valve Controller, ASi Communication with Extended Addressing, SS tubing & fittings, SS TAG |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4719A |  | XV-4719A | PMP-F-47-50-02 | Fryer A | Ball Valve - Filter #2 Drain | Solenoid | 2" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, Axiom AN Valve Controller, ASi Communication with Extended Addressing, SS tubing & fittings, SS TAG |  |  |  | GEM | GEM | Elec. Contractor
| SV | 4720A |  | SV-4720A | PMP-F-47-50-02 | Fryer A | Solenoid Valve - PUMP Seal Water 1/2"NPT | Solenoid | ASCO VALVE, 1/2"-NPT, P/N #8210G087 |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4722A |  | XV-4722A | PMP-F-47-50-02 | Fryer A | Ball Valve - Drain to Floor | Solenoid | 4" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, Axiom AN Valve Controller, ASi Communication with Extended Addressing, SS tubing & fittings, SS TAG |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4722B |  | XV-4722B | PMP-F-47-50-02 | Fryer A | Ball Valve - A-Stage LP Pump Volute Drain | Solenoid | 3/4" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, Axiom AN Valve Controller, ASi Communication with Extended Addressing, SS tubing & fittings, SS TAG |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4722C |  | XV-4722C | PMP-F-47-50-02 | Fryer A | Ball Valve - LP Pump By-Pass | Solenoid | 1" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, |  |  |  | GEM | GEM | Elec. Contractor
| TE | 4730A |  | TE-4730A | PMP-F-47-50-03 | Heat Exchanger A | Oil Inlet Temperature | Temperature Transmitter | E+H,MODEL #TH13-2B12E1B531AK , 4.5" IMMERSION W/3" LAG, 3 WIRE, 316SS HOUSING, TERMINAL BLOCK. |  |  |  | GEM | GEM | Elec. Contractor
| PIT | 4730A |  | PIT-4730A | PMP-F-47-50-03 | Lakos Filter A | Inlet Oil Pressure | Pressure Transmitter | PMP75-XBT1P11AF3AU |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4730A |  | XV-4730A | PMP-F-47-50-03 | Fryer A | Ball Valve - Lakos Purge | Solenoid | 3" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, Axiom AN Valve Controller, ASi Communication with Extended Addressing, SS tubing & fittings, SS TAG |  |  |  | GEM | GEM | Elec. Contractor
| PIT | 4730B |  | PIT-4730B | PMP-F-47-50-03 | Lakos Filter A | Outlet Oil Pressure | Pressure Transmitter | PMP75-XBT1P11AF3AU |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4730B |  | XV-4730B | PMP-F-47-50-03 | Fryer A | Ball Valve - Lakos Drain | Solenoid | 1" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4730C |  | XV-4730C | PMP-F-47-50-03 | Fryer A | Ball Valve - Stack CIP | Solenoid | 2" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, Axiom AN Valve Controller, ASi Communication with Extended Addressing, SS tubing & fittings, SS TAG |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4730D |  | XV-4730D | PMP-F-47-50-03 | Fryer A | Ball Valve - Main CIP | Solenoid | 4" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, Axiom AN Valve Controller, ASi Communication with Extended Addressing, SS tubing & fittings, SS TAG |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4730E |  | XV-4730E | PMP-F-47-50-03 | Fryer A | Ball Valve - Main CIP | Solenoid | 4" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, Axiom AN Valve Controller, ASi Communication with Extended Addressing, SS tubing & fittings, SS TAG |  |  |  | GEM | GEM | Elec. Contractor
| TCV | 4732A |  | TCV-4732A | PMP-F-47-50-03 | Heat Exchanger A | Steam Inlet Valve | Temperature Valve | Steam Valve, 4" Fisher 667-ET-DVC6200 4-20 Hart, with 300# RF, CS Body |  |  |  | GEM | OTHERS | Elec. Contractor
| LCV | 4732A |  | LCV-4732A | PMP-F-47-50-03 | Heat Exchanger A | Condensate Level | Level Valve | Condensate Valve, 1" Fisher 657-EAS-DVC6200 4-20 Hart, with 300# RF, CS Body |  |  |  | GEM | OTHERS | Elec. Contractor
| LIT | 4732 |  | LIT-4732 | PMP-F-47-50-03 | Heat Exchanger A | Condensate Level | Level Transmitter | FMD78-UB37F41AR3EU |  |  |  | GEM | GEM | Elec. Contractor
| TE | 4732A |  | TE-4732A | PMP-F-47-50-03 | Heat Exchanger A | Oil Outlet Temperature | Temperature Transmitter | E+H,MODEL #TH13-2B12E1B531AK , 4.5" IMMERSION W/3" LAG, 3 WIRE, 316SS HOUSING, TERMINAL BLOCK. |  |  |  | GEM | GEM | Elec. Contractor
| FIT | 4732A |  | FIT-4732A | PMP-F-47-50-03 | Fryer A | Flow Meter A | Flow Transmitter 10" | FLOWMETER, PROWIRL F 200, 7F2C2F-C4BCJCDBAAAAASKA1+AA 10" (DN250), W/150# RFSO ENDS, 4-20mA HART, 10m REMOTE MOUNT ELECTRONICS, HIGH TEMP 750°F |  |  |  | GEM | GEM | Elec. Contractor
| FV | 4732 |  | FV-4732 | PMP-F-47-50-03 | Fryer A | By-Pass Line Flow | Flow Valve 6" | VAC Model D400-D-N-D2-H-4/20-SStag |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4732A |  | XV-4732A | PMP-F-47-50-03 | Fryer A | Ball Valve - HX Inlet Vent | Solenoid | 1" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, |  |  |  | GEM | GEM | Elec. Contractor
| PIT | 4732B |  | PIT-4732B | PMP-F-47-50-03 | Fryer Kettle A | Inlet Oil Pressure | Pressure Transmitter | PMP75-XBT1P11AF3AU |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4732B |  | XV-4732B | PMP-F-47-50-03 | Fryer A | Ball Valve - HX Outlet Vent | Solenoid | 1" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4732C |  | XV-4732C | PMP-F-47-50-03 | Fryer A | Ball Valve - Inlet header Drain | Solenoid | 3" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, Axiom AN Valve Controller, ASi Communication with Extended Addressing, SS tubing & fittings, SS TAG |  |  |  | GEM | GEM | Elec. Contractor
| LIT | 4735A |  | LIT-4735A | PMP-F-47-50-03 | Fryer Oil Purge Tank A | Purge Tank A | Pressure Transmitter | FMD77-UB37D41DQVAG |  |  |  | GEM | GEM | Elec. Contractor
| LSH | 4735A |  | LSH-4735A | PMP-F-47-50-03 | Purge Tank A | High Level | Level Switch | ENDRESS & HAUSER, LIQUIPHANT LEVEL SWITCH, MODEL #FTL71-UGM2CB4E6AL,PROBE LENGTH = 6", PROCESS CONNECTION = NPT 3/4", 316 S.S. W/ HOUSING TAG |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4735A |  | XV-4735A | PMP-F-47-50-03 | Fryer A | Ball Valve - Stage A Purge Tank Drain | Solenoid | 3" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, Axiom AN Valve Controller, ASi Communication with Extended Addressing, SS tubing & fittings, SS TAG |  |  |  | GEM | GEM | Elec. Contractor
| LCV | 4745A |  | LCV-4745A | PMP-F-47-50-04 | Fryer B | Oil Make Up Valve | Control Valve 1" | 1" Fisher Control Valve, 1" 32-24588SVF DVC6200 316SS, Stainless Steel Body, Flanged 300# ANSI Rated, Seal Metal / Packing = Spring Loaded PTFE, Equal Percent / Fail close Actuator / DVC-620 4-20 Hart, Designed to handle 400 F Hot Cooking Oil |  |  |  | GEM | GEM | Elec. Contractor
| ZS | 4745A |  | ZS-4745A | PMP-F-47-50-04 | CONNECTION TANK | CIP Disconnect | Saftey Switch | Allen-Bradley Magnetically CodedMC2 , 2 N.C. Solid-State Relay Safety Outputs 1 x PNP (0.2 A max), Status: OFF (0V DC) Aux Outputs ,, LED Indicator,6 inch Pigtail with 8-Pin Micro (M12) Connector PRT# 440N-Z21W1PH |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4747A |  | XV-4747A | PMP-F-47-50-04 | Fryer B | Ball Valve - Filter #1 Drain | Solenoid | 2" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, Axiom AN Valve Controller, ASi Communication with Extended Addressing, SS tubing & fittings, SS TAG |  |  |  | GEM | GEM | Elec. Contractor
| ZSS | 4747A |  | ZSS-4747A | PMP-F-47-50-04 | Fryer B Rosenqvist | [6 empty] | OTHERS | OTHERS | Elec. Contractor
| XV | 4748 |  | XV-4748 | PMP-F-47-50-02 | Fryer A | Steam Quench | Solenoid | 1/2" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, Axiom AN Valve Controller, ASi Communication with Extended Addressing, SS tubing & fittings, SS TAG |  |  |  | GEM | GEM | Elec. Contractor
| FS | 4748A |  | FS-4748A | PMP-F-47-50-04 | Circ Pump Stage B | Water Flush Flowmeter | FLOWMETER SWITCH | 1/2" NPT FLOW SWITCH, "FLOTECT", V6EPS-S-S-1-S-MT SERIES V6 FLOW SWITCH, EP = EXPLOSION PROOF, S = STAINLESS STEEL UPPER BODY, S = STAINLESS STEEL LOWER BODY, S = SPDT CIRCUIT (SWITCH), 1 = 1/2" NPT (TEE CONNECTION SIZE), S = STAINLESS STEEL TEE, MT = HIGH TEMPERATURE OPTION RATED FOR 400° F |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4748A |  | XV-4748A | PMP-F-47-50-04 | Fryer B | Ball Valve - Pump #1 Volute Drain | Solenoid | 3/4" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, Axiom AN Valve Controller, ASi Communication with Extended Addressing, SS tubing & fittings, SS TAG |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4748B |  | XV-4748B | PMP-F-47-50-04 | Fryer B | Ball Valve - Main LP Drain | Solenoid | 4" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, Axiom AN Valve Controller, ASi Communication with Extended Addressing, SS tubing & fittings, SS TAG |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4749A |  | XV-4749A | PMP-F-47-50-04 | Fryer B | Ball Valve - Filter #2 Drain | Solenoid | 2" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, Axiom AN Valve Controller, ASi Communication with Extended Addressing, SS tubing & fittings, SS TAG |  |  |  | GEM | GEM | Elec. Contractor
| ZSS | 4749A |  | ZSS-4749A | PMP-F-47-50-04 | Fryer B Rosenqvist | [6 empty] | OTHERS | OTHERS | Elec. Contractor
| SV | 4750A |  | SV-4750A | PMP-F-47-50-04 | Fryer B | Solenoid Valve - PUMP Seal Water 1/2"NPT | Solenoid | ASCO VALVE, 1/2"-NPT, P/N #8210G087 |  |  |  | GEM | GEM | Elec. Contractor
| FS | 4748A |  | FS-4748A | PMP-F-47-50-04 | Circ Pump Stage B | Water Flush Flowmeter | FLOWMETER SWITCH | 1/2" NPT FLOW SWITCH, "FLOTECT", V6EPS-S-S-1-S-MT SERIES V6 FLOW SWITCH, EP = EXPLOSION PROOF, S = STAINLESS STEEL UPPER BODY, S = STAINLESS STEEL LOWER BODY, S = SPDT CIRCUIT (SWITCH), 1 = 1/2" NPT (TEE CONNECTION SIZE), S = STAINLESS STEEL TEE, MT = HIGH TEMPERATURE OPTION RATED FOR 400° F |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4753A |  | XV -4753A | PMP-F-47-50-04 | Fryer B | Ball Valve - Drain to Floor | Solenoid | 4" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, Axiom AN Valve Controller, ASi Communication with Extended Addressing, SS tubing & fittings, SS TAG |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4753B |  | XV-4753B | PMP-F-47-50-04 | Fryer B | Ball Valve - B-Stage LP Pump Volute Drain | Solenoid | 3/4" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, Axiom AN Valve Controller, ASi Communication with Extended Addressing, SS tubing & fittings, SS TAG |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4753C |  | XV-4753C | PMP-F-47-50-04 | Fryer B | Ball Valve - LP Pump By-Pass | Solenoid | 1" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, |  |  |  | GEM | GEM | Elec. Contractor
| SS | 4755A |  | SS-4755A | PMP-F-47-50-04 | Crumb Auger | Auger Shaft Rotaion Detction | Proximity Switch | PROXIMITY SUITCHES, #871TM-BH8N18-N3 MINI-CHANGE STYLE, AC/DC 20-240 VAC, ALLEN-BRADLEY |  |  |  | GEM | GEM | Elec. Contractor
| SS | 4757A |  | SS-4757A | PMP-F-47-50-04 | Crumb Auger | Auger Shaft Rotaion Detction | Proximity Switch | PROXIMITY SUITCHES, #871TM-BH8N18-N3 MINI-CHANGE STYLE, AC/DC 20-240 VAC, ALLEN-BRADLEY |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4757 |  | XV-4757 | PMP-F-47-50-04 | CRUMB PRESS | Knife Valve | Solenoid | VAC Model D400-D-N-D2-H-4/20-SStag |  |  |  | GEM | GEM | Elec. Contractor
| TE | 4765A |  | TE-4765A | PMP-F-47-50-05 | Fryer B | Oil Inlet Temperature | Temperature Transmitter | E+H,MODEL #TH13-2B12E1B531AK , 4.5" IMMERSION W/3" LAG, 3 WIRE, 316SS HOUSING, TERMINAL BLOCK. |  |  |  | GEM | GEM | Elec. Contractor
| PIT | 4765A |  | PIT-4765A | PMP-F-47-50-05 | Lakos Filter B | Inlet Oil Pressure | Pressure Transmitter | PMP75-XBT1P11AF3AU |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4765A |  | XV-4765A | PMP-F-47-50-05 | Fryer B | Ball Valve - Lakos Purge | Solenoid | 3" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, Axiom AN Valve Controller, ASi Communication with Extended Addressing, SS tubing & fittings, SS TAG |  |  |  | GEM | GEM | Elec. Contractor
| PIT | 4765B |  | PIT-4765B | PMP-F-47-50-05 | Lakos Filter B | Outlet Oil Pressure | Pressure Transmitter | PMP75-XBT1P11AF3AU |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4765B |  | XV-4765B | PMP-F-47-50-05 | Fryer B | Ball Valve - Lakos Drain | Solenoid | 1" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4765C |  | XV-4765C | PMP-F-47-50-05 | Fryer B | Ball Valve - Stack CIP | Solenoid | 2" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, Axiom AN Valve Controller, ASi Communication with Extended Addressing, SS tubing & fittings, SS TAG |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4765D |  | XV-4765D | PMP-F-47-50-05 | Fryer B | Ball Valve - Main CIP | Solenoid | 4" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, Axiom AN Valve Controller, ASi Communication with Extended Addressing, SS tubing & fittings, SS TAG |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4765E |  | XV-4765E | PMP-F-47-50-05 | Fryer B | Ball Valve - Main CIP | Solenoid | 4" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, Axiom AN Valve Controller, ASi Communication with Extended Addressing, SS tubing & fittings, SS TAG |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4765F |  | XV-4765F | PMP-F-47-50-05 | Fryer A/B | Transition CIP | Solenoid | 3" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, Axiom AN Valve Controller, ASi Communication with Extended Addressing, SS tubing & fittings, SS TAG |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4765G |  | XV-4765G | PMP-F-47-50-05 | Fryer B | Ball Valve - Stack CIP | Solenoid | 2" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, Axiom AN Valve Controller, ASi Communication with Extended Addressing, SS tubing & fittings, SS TAG |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4765H |  | XV-4765H | PMP-F-47-50-05 | Fryer B | Ball Valve - Oil Miser Take-off | Solenoid | 2" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, Axiom AN Valve Controller, ASi Communication with Extended Addressing, SS tubing & fittings, SS TAG |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4765J |  | XV-4765J | PMP-F-47-50-05 | Fryer B | Drip Pan Flush | Solenoid | 1-1/2" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, Axiom AN Valve Controller, ASi Communication with Extended Addressing, SS tubing & fittings, SS TAG |  |  |  | GEM | GEM | Elec. Contractor
| TCV | 4767A |  | TCV-4767A | PMP-F-47-50-05 | Heat Exchanger B | Steam Inlet Valve | Temperature Valve | Steam Valve, 6" Fisher 667-ET-DVC6200 4-20 Hart, with 300# RF, CS Body |  |  |  | GEM | OTHERS | Elec. Contractor
| LCV | 4767A |  | LCV-4767A | PMP-F-47-50-05 | Heat Exchanger B | Condensate Level | Level Valve | Condensate Valve, 2" Fisher 657-EAS-DVC6200 4-20 Hart, with 300# RF, CS Body |  |  |  | GEM | OTHERS | Elec. Contractor
| LIT | 4767 |  | LIT-4767 | PMP-F-47-50-05 | Heat Exchanger B | Condensate Level | Level Transmitter | FMD78-UB37F41AR3EU |  |  |  | GEM | GEM | Elec. Contractor
| TE | 4767A |  | TE-4767A | PMP-F-47-50-05 | Fryer B | Oil Outlet Temperature | Temperature Transmitter | E+H,MODEL #TH13-2B12E1B531AK , 4.5" IMMERSION W/3" LAG, 3 WIRE, 316SS HOUSING, TERMINAL BLOCK. |  |  |  | GEM | GEM | Elec. Contractor
| FIT | 4767A |  | FIT-4767A | PMP-F-47-50-05 | Fryer B | Flow Meter B | Flow Transmitter 12" | FLOWMETER, PROWIRL F 200, 7F2C3H-C4BCJCDBAAAAASKA1+AA 12" (DN300), W/150# RFSO ENDS, 4-20mA HART, 10m REMOTE MOUNT ELECTRONICS, HIGH TEMP 750°F |  |  |  | GEM | GEM | Elec. Contractor
| FV | 4767 |  | FV-4767 | PMP-F-47-50-05 | Fryer B | By-Pass Line Flow | Flow Valve 6" | VAC Model D400-D-N-D2-H-4/20-SStag |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4767A |  | XV-4767A | PMP-F-47-50-05 | Fryer B | Ball Valve - HX Inlet Vent | Solenoid | 1" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, |  |  |  | GEM | GEM | Elec. Contractor
| PIT | 4767B |  | PIT-4767B | PMP-F-47-50-05 | Fryer Kettle B | Inlet Oil Pressure | Pressure Transmitter | PMP75-XBT1P11AF3AU |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4767B |  | XV-4767B | PMP-F-47-50-05 | Fryer B | Ball Valve - HX Outlet Vent | Solenoid | 1" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4767C |  | XV-4767C | PMP-F-47-50-05 | Fryer B | Ball Valve - Inlet header Drain | Solenoid | 3" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, Axiom AN Valve Controller, ASi Communication with Extended Addressing, SS tubing & fittings, SS TAG |  |  |  | GEM | GEM | Elec. Contractor
| LIT | 4770A |  | LIT-4770A | PMP-F-47-50-05 | Fryer Oil Purge Tank B | Pressure Transmitter | Pressure Transmitter | FMD77-UB37D41DQVAG |  |  |  | GEM | GEM | Elec. Contractor
| LSH | 4770A |  | LSH-4770A | PMP-F-47-50-05 | Purge Tank B | High Level | Level Switch | ENDRESS & HAUSER, LIQUIPHANT LEVEL SWITCH, MODEL #FTL71-UGM2CB4E6AL,PROBE LENGTH = 6", PROCESS CONNECTION = NPT 3/4", 316 S.S. W/ HOUSING TAG |  |  |  | GEM | GEM | Elec. Contractor
| XV | 4770A |  | XV-4770A | PMP-F-47-50-05 | Fryer B | Ball Valve - Stage B Purge Tank Drain | Solenoid | 3" Flo-Tite 3 Piece Ball Valve, Full Port, Extended Butt Weld Ends facilitates weld in place without valve disassembly, Hi-Temp Seats, Ball vented to DOWNSTREAM side, with Nickel Infused Spring Return Actuator, Fail Closed, Axiom AN Valve Controller, ASi Communication with Extended Addressing, SS tubing & fittings, SS TAG |  |  |  | GEM | GEM | Elec. Contractor
-
-
-
|  | Preliminary |  |  |  |  | DESCRIPTION | [7 empty] | BY | DATE
|  | Confirmed |  |  |  |  | Created
|  | Educated Guess |  |  |  |  | Revised
NEW
Changed

## Motor
REV | ISA | AREA No. | LOOP | ID # | P&ID DWG. # | AREA | DESCRIPTION | MOTOR DATA |  |  | MOTOR DATA |  | GEAR BOX DATA |  | STARTER DATA |  |  |  |  | MOTOR RESPONSIBILITY
[8 empty] | VOLT | HP | FLA | BRAND | MODEL # | BRAND | MODEL # | MCC | TYPE | BKR | O/L | NODE | SUPPLY | INSTALL | CONNECT
| M | 4705A |  | M-4705A | PMP-F-47-50-01 | Fryer | Conveyor Fryer Belt Stage A | 460 | 7.5 | 9 | Toshiba | Y754XDSB44A-P | SEW | KT87AM213/215 |  | VFD |  |  |  | GEM | GEM | Elect. Contractor
| M | 4710A |  | M-4710A | PMP-F-47-50-01 | Fryer | Conveyor Fryer Belt Stage B | 460 | 5 | 6.1 | Toshiba | 0054XDSB44A-P | SEW | KT97AM184 |  | VFD |  |  |  | GEM | GEM | Elect. Contractor
| M | 4718A |  | M-4718A | PMP-F-47-50-02 | Fryer | Recirculation Pump #1 Stage A | 460 | 200 |  | Toshiba | 206XDSB41A |  |  |  | VFD |  |  |  | GEM | GEM | Elect. Contractor
| M | 4748A |  | M-4748A | PMP-F-47-50-04 | Fryer | Recirculation Pump #1 Stage B | 460 | 200 |  | Toshiba | 206XDSB41A |  |  |  | VFD |  |  |  | GEM | GEM | Elect. Contractor
| M | 4707A |  | M-4707A | PMP-F-47-50-01 | Fryer | Hood Jack Motor | 460 | 7.5 | 9 | Toshiba | Y754XDSB44A-P | SEW | K77AM213/215 |  | VFD |  |  |  | GEM | GEM | Elect. Contractor
| M | 4714A |  | M-4714A | PMP-F-47-50-01 | Fryer | Drip Pan Pump # 1 | 460 | 5 | 6.1 | Toshiba | 0054XDSB42A-P |  |  |  | FVNR |  |  |  | GEM | GEM | Elect. Contractor
| M | 4713A |  | M-4713A | PMP-F-47-50-01 | Fryer | Drip Pan Pump # 2 | 460 | 15 | 17 | Toshiba | 0154XDSB44A-P |  |  |  | FVNR |  |  |  | GEM | GEM | Elect. Contractor
| M | 4717A |  | M-4717A | PMP-F-47-50-02 | Fryer | Filter #1 Stage A Motor | 460 | 1 | 1.7 | [5 empty] | FVNR |  |  |  | Simplot | GEM | Elect. Contractor
| M | 4717B |  | M-4717B | PMP-F-47-50-02 | Fryer | Filter #1 Stage A AUGER Motor | 460 | 1 | 1.7 | [5 empty] | FVNR |  |  |  | Simplot | GEM | Elect. Contractor
| M | 4719A |  | M-4719A | PMP-F-47-50-02 | Fryer | Filter #2 Stage A Motor | 460 | 1 | 1.7 | [5 empty] | FVNR |  |  |  | Simplot | GEM | Elect. Contractor
| M | 4719B |  | M-4719B | PMP-F-47-50-02 | Fryer | Filter #2 Stage A AUGER Motor | 460 | 1 | 1.7 | [5 empty] | FVNR |  |  |  | Simplot | GEM | Elect. Contractor
| M | 4747A |  | M-4747A | PMP-F-47-50-04 | Fryer | Filter #1 Stage B Motor | 460 | 1 | 1.7 | [5 empty] | FVNR |  |  |  | Simplot | GEM | Elect. Contractor
| M | 4747B |  | M-4747B | PMP-F-47-50-04 | Fryer | Filter #1 Stage B AUGER Motor | 460 | 1 | 1.7 | [5 empty] | FVNR |  |  |  | Simplot | GEM | Elect. Contractor
| M | 4749A |  | M-4749A | PMP-F-47-50-04 | Fryer | Filter #2 Stage B Motor | 460 | 1 | 1.7 | [5 empty] | FVNR |  |  |  | Simplot | GEM | Elect. Contractor
| M | 4749B |  | M-4749B | PMP-F-47-50-04 | Fryer | Filter #2 Stage B AUGER Motor | 460 | 1 | 1.7 | [5 empty] | FVNR |  |  |  | Simplot | GEM | Elect. Contractor
| M | 4722A |  | M-4722A | PMP-F-47-50-02 | Fryer | Stage A Pump Down Pump | 460 | 15 | 17 | Toshiba | 0154XDSB44A-P | SEW | RX97AM254/256 |  | FVNR |  |  |  | GEM | GEM | Elect. Contractor
| M | 4753A |  | M-4753A | PMP-F-47-50-04 | Fryer | Stage B Pump Down Pump | 460 | 15 | 17 | Toshiba | 0154XDSB44A-P | SEW | RX97AM254/256 |  | FVNR |  |  |  | GEM | GEM | Elect. Contractor
| M | 4706A |  | M-4706A | PMP-F-47-50-01 | Fryer | Infeed End Hood Baffle | 460 | 1 | 1.7 | Toshiba | 0014SDBA42A-P | SEW | R37AM143 |  | VFD |  |  |  | GEM | GEM | Elect. Contractor
| M | 4755A |  | M-4755A | PMP-F-47-50-04 | Fryer | Fryer Crumb Auger | 460 | 1 | 1.7 | Toshiba | 0014XDSB44AP | SEW | KA37TAM143 |  | VFD |  |  |  | GEM | GEM | Elect. Contractor
| M | 4757A |  | M-4757A | PMP-F-47-50-04 | Fryer | Fryer Crumb Incline Auger | 460 | 1 | 1.7 | Toshiba | 0014XDSB44AP | SEW | KA37TAM143 |  | VFD |  |  |  | GEM | GEM | Elect. Contractor
| M | 4758A |  | M-4758A | PMP-F-47-50-04 | Fryer | Crumb PRESS | 460 | 10 | 11 | SEW | DRN132M4 | SEW | FTF107AM213/215 |  | VFD |  |  |  | GEM | GEM | Elect. Contractor
|  | Preliminary |  |  |  |  | DESCRIPTION | [7 empty] | BY | DATE
|  | Confirmed |  |  |  |  | Created | [7 empty] | BWW | 8-31-18
|  | Educated Guess |  |  |  |  | Revised | [7 empty] | BWW | 12-18-18
NEW
Changed