## Motor List
REV | LOAD TAG NUMBER | EQUIPMENT DESCRIPTION | COMMENTS | P&ID | MOTOR HP | MOTOR FLA | VFD/FVNR | Type | SUPPLIED BY | MCC or PANEL SOURCE | MCC SECTION | ETHERNET DROP | CABLE TAG | CABLE TYPE | LINE | UNIT | UNIT DESC | PID LAYER | Status
| EC-4006A | L4 PEELER B FD CNVR-1 |  | GFP-F-40-50-01 | 5 |  | VFD | EXISTING | [6 empty] | 4 | OEM |  | Equipment-Modified
| EC-4008A | L4 PEELER B FD CNVR-2 |  | GFP-F-40-50-01 | 5 |  | VFD | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-4010A | L4 PEELER B ROTARY FD HOPPER |  | GFP-F-40-50-01 | 2 |  | VFD | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-4011A | L4 PEELER B |  | GFP-F-40-50-01 | 5 |  | VFD | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-4015A | L4 PEELER B DISCH AUGER |  | GFP-F-40-50-01 | 7.5 |  | VFD | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-4016A | L4 PEELER B DISCH TRANSFER CNVR |  | GFP-F-40-50-01 | ? |  | ? | EXISTING | [6 empty] | 4 | OEM |  | Equipment-Existing
| EC-4082A | L4 PEF FD DEWTRING SHKR |  | GFP-F-40-50-02-New | 4.8 |  | FVNR | MotorE300 | [6 empty] | 4 | L4_PEF | LINE 4 PEF UNIT | Equipment - Vendor Supplied Items
| EC-4085A | L4 PEF FD RETURN WTR PMP |  | GFP-F-40-50-02-New | 20 |  | VFD | PF52x | [6 empty] | 4 | L4_PEF | LINE 4 PEF UNIT | Equipment-Relocated
| EC-4087A | L4 PEF BELT |  | GFP-F-40-50-02-New | 2 |  | VFD | PF52x | [6 empty] | 4 | L4_PEF | LINE 4 PEF UNIT | Equipment - Vendor Supplied Items
| EC-4090A | L4 PEF CIP PMP |  | GFP-F-40-50-02-New | 7.5 |  | VFD | PF52x | [6 empty] | 4 | L4_PEF | LINE 4 PEF UNIT | Equipment - Vendor Supplied Items
| EC-4461A | L4 SAPP PRODUCT PMP |  | GFP-F-44-50-01-New | 15 |  | VFD | PF52x | [6 empty] | 4 | L4_SAPP | LINE 4 SAPP UNIT | Equipment - Vendor Supplied Items
| EC-4463A | L4 SAPP DEWTRING SHKR |  | GFP-F-44-50-01-New | 4.8 |  | FVNR | MotorE300 | [6 empty] | 4 | L4_SAPP | LINE 4 SAPP UNIT | Equipment - Vendor Supplied Items
| EC-4470A | L4 DRYER FD SHKR |  | GFP-F-44-50-01-New | 3 |  | FVNR | MotorE300 | [6 empty] | 4 | L4_SAPP | LINE 4 SAPP UNIT | Equipment - Vendor Supplied Items
| EC-4505A | L4 DRYER STAGE A BELT |  | GFP-F-45-50-01 | 1.5 |  | VFD | PF52x | [6 empty] | 4 | L4_DRYER | LINE 4 DRYER UNIT | Equipment - Vendor Supplied Items
| EC-4505B | L4 DRYER STAGE A BELT MTR FAN |  | GFP-F-45-50-01 | 0.1 |  | FVNR | MotorE300 | [6 empty] | 4 | L4_DRYER | LINE 4 DRYER UNIT | Equipment - Vendor Supplied Items
| EC-4510A | L4 DRYER ZONE 1 RECIRC FAN 1 |  | GFP-F-45-50-01 | 40 |  | VFD | PF755 | [6 empty] | 4 | L4_DRYER | LINE 4 DRYER UNIT | Equipment - Vendor Supplied Items
| EC-4511A | L4 DRYER ZONE 1 RECIRC FAN 2 |  | GFP-F-45-50-01 | 40 |  | VFD | PF755 | [6 empty] | 4 | L4_DRYER | LINE 4 DRYER UNIT | Equipment - Vendor Supplied Items
| EC-4518A | L4 DRYER ZONE 1 EXHAUST FAN |  | GFP-F-45-50-01 | 15 |  | VFD | PF52x | [6 empty] | 4 | L4_DRYER | LINE 4 DRYER UNIT | Equipment - Vendor Supplied Items
| EC-4520A | L4 DRYER ZONE 2 RECIRC FAN 1 |  | GFP-F-45-50-01 | 40 |  | VFD | PF755 | [6 empty] | 4 | L4_DRYER | LINE 4 DRYER UNIT | Equipment - Vendor Supplied Items
| EC-4521A | L4 DRYER ZONE 2 RECIRC FAN 2 |  | GFP-F-45-50-01 | 40 |  | VFD | PF755 | [6 empty] | 4 | L4_DRYER | LINE 4 DRYER UNIT | Equipment - Vendor Supplied Items
| EC-4528A | L4 DRYER ZONE 2 EXHAUST FAN |  | GFP-F-45-50-01 | 15 |  | VFD | PF52x | [6 empty] | 4 | L4_DRYER | LINE 4 DRYER UNIT | Equipment - Vendor Supplied Items
| EC-4535A | L4 DRYER STAGE B BELT |  | GFP-F-45-50-02 | 1.5 |  | VFD | PF52x | [6 empty] | 4 | L4_DRYER | LINE 4 DRYER UNIT | Equipment - Vendor Supplied Items
| EC-4535B | L4 DRYER STAGE B BELT MTR FAN |  | GFP-F-45-50-02 | 0.1 |  | FVNR | MotorE300 | [6 empty] | 4 | L4_DRYER | LINE 4 DRYER UNIT | Equipment - Vendor Supplied Items
| EC-4540A | L4 DRYER ZONE 3 RECIRC FAN 1 |  | GFP-F-45-50-02 | 30 |  | VFD | PF755 | [6 empty] | 4 | L4_DRYER | LINE 4 DRYER UNIT | Equipment - Vendor Supplied Items
| EC-4541A | L4 DRYER ZONE 3 RECIRC FAN 2 |  | GFP-F-45-50-02 | 30 |  | VFD | PF755 | [6 empty] | 4 | L4_DRYER | LINE 4 DRYER UNIT | Equipment - Vendor Supplied Items
| EC-4542A | L4 DRYER ZONE 3 RECIRC FAN 3 |  | GFP-F-45-50-02 | 30 |  | VFD | PF755 | [6 empty] | 4 | L4_DRYER | LINE 4 DRYER UNIT | Equipment - Vendor Supplied Items
| EC-4548A | L4 DRYER ZONE 3 EXHAUST FAN |  | GFP-F-45-50-02 | 15 |  | VFD | PF52x | [6 empty] | 4 | L4_DRYER | LINE 4 DRYER UNIT | Equipment - Vendor Supplied Items
| EC-4550A | L4 DRYER ZONE 4 RECIRC FAN 1 |  | GFP-F-45-50-02 | 30 |  | VFD | PF755 | [6 empty] | 4 | L4_DRYER | LINE 4 DRYER UNIT | Equipment - Vendor Supplied Items
| EC-4551A | L4 DRYER ZONE 4 RECIRC FAN 2 |  | GFP-F-45-50-02 | 30 |  | VFD | PF755 | [6 empty] | 4 | L4_DRYER | LINE 4 DRYER UNIT | Equipment - Vendor Supplied Items
| EC-4552A | L4 DRYER ZONE 4 RECIRC FAN 2 |  | GFP-F-45-50-02 | 30 |  | VFD | PF755 | [6 empty] | 4 | L4_DRYER | LINE 4 DRYER UNIT | Equipment - Vendor Supplied Items
| EC-4558A | L4 DRYER ZONE 4 EXHAUST FAN |  | GFP-F-45-50-02 | 15 |  | VFD | PF52x | [6 empty] | 4 | L4_DRYER | LINE 4 DRYER UNIT | Equipment - Vendor Supplied Items
| EC-4565A | L4 DRYER CIP RETURN PMP |  | GFP-F-45-50-02 | 15 |  | VFD | PF52x | [6 empty] | 4 | L4_DRYER | LINE 4 DRYER UNIT | PID
| EC-4568A | L5 DRYER DISCH SHKR |  | GFP-F-45-50-02 | 4.8 |  | FVNR | MotorE300 | [6 empty] | 4 | L4_DRYER | LINE 4 DRYER UNIT | Equipment - Vendor Supplied Items
| EC-4574A | L4 DRYER DISCH INCLINE CNVR |  | GFP-F-45-50-02 | 5 |  | VFD | PF52x | [6 empty] | 4 | L4_DRYER | LINE 4 DRYER UNIT | Equipment - Vendor Supplied Items
| EC-4611A | BATTER WTR RECIRCULATION PMP |  | GFP-F-46-50-01 | 2 |  | VFD | PF52x | [6 empty] | 4 | L4_BATTER | LINE 4 BATTER UNIT | Equipment - Vendor Supplied Items
| EC-4615A | BEER UNLOADING PMP |  | GFP-F-46-50-01 | 20 |  | VFD | PF52x | [6 empty] | 4 | L4_BATTER | LINE 4 BATTER UNIT | Equipment - Vendor Supplied Items
| EC-4618A | BEER SUPPLY PMP |  | GFP-F-46-50-01 | 7.5 |  | VFD | PF52x | [6 empty] | 4 | L4_BATTER | LINE 4 BATTER UNIT | Equipment - Vendor Supplied Items
| EC-4625A | L4 BATTER HOIST TROLLEY |  | GFP-F-46-50-02 | 0.5 |  | FVR | MotorRev | [6 empty] | 4 | L4_BATTER | LINE 4 BATTER UNIT | Equipment - Vendor Supplied Items
| EC-4625B | L4 BATTER HOIST |  | GFP-F-46-50-02 | 2.4 |  | FVR | MotorRev | [6 empty] | 4 | L4_BATTER | LINE 4 BATTER UNIT | Equipment - Vendor Supplied Items
| EC-4628A | L4 BATTER BAG DUST COLLECTOR |  | GFP-F-46-50-02 | 2 |  | FVNR | MotorE300 | [6 empty] | 4 | L4_BATTER | LINE 4 BATTER UNIT | Equipment - Vendor Supplied Items
| EC-4632A | L4 BATTER BAG UNLOADER AUGER |  | GFP-F-46-50-02 | 5 |  | VFD | PF52x | [6 empty] | 4 | L4_BATTER | LINE 4 BATTER UNIT | Equipment - Vendor Supplied Items
| EC-4656A | L4 BATTER WEIGH HOPPER ROTARY VALVE |  | GFP-F-46-50-03 | 1 |  | VFD | PF52x | [6 empty] | 4 | L4_BATTER | LINE 4 BATTER UNIT | Equipment - Vendor Supplied Items
| EC-4660A | L4 BATTER MIX TNK MIXER |  | GFP-F-46-50-03 | 60 |  | VFD | PF755 | [6 empty] | 4 | L4_BATTER | LINE 4 BATTER UNIT | Equipment - Vendor Supplied Items
| EC-4662A | L4 MIXED BATTER TRANSFER PMP |  | GFP-F-46-50-03 | 50 |  | VFD | PF755 | [6 empty] | 4 | L4_BATTER | LINE 4 BATTER UNIT | Equipment - Vendor Supplied Items
| EC-4665A | L4 BATTER HOLDING TNK MIXER |  | GFP-F-46-50-04 | 5 |  | VFD | PF52x | [6 empty] | 4 | L4_BATTER | LINE 4 BATTER UNIT | Equipment - Vendor Supplied Items
| EC-4666A | L4 BATTER HOLDING TNK PMP |  | GFP-F-46-50-04 | 10 |  | VFD | PF52x | [6 empty] | 4 | L4_BATTER | LINE 4 BATTER UNIT | Equipment - Vendor Supplied Items
| EC-4677A | L4 BATTER APPLICATOR BIAS SHKR |  | GFP-F-46-50-05 | 3 |  | FVNR | MotorE300 | [6 empty] | 4 | L4_BATTER | LINE 4 BATTER UNIT | Equipment - Vendor Supplied Items
| EC-4680A | L4 BATTER APPLICATOR FD SHKR |  | GFP-F-46-50-05 | 5 |  | FVNR | MotorE300 | [6 empty] | 4 | L4_BATTER | LINE 4 BATTER UNIT | Equipment - Vendor Supplied Items
| EC-4680C | L4 BATTER APPLICATOR FD SHKR TROLLEY |  | GFP-F-46-50-05 | 1 |  | FVR | MotorRev | [6 empty] | 4 | L4_BATTER | LINE 4 BATTER UNIT | Equipment - Vendor Supplied Items
| EC-4685A | L4 BATTER APPLICATOR HOOD JACK |  | GFP-F-46-50-05 | 3 |  | VFD | PF52x | [6 empty] | 4 | L4_BATTER | LINE 4 BATTER UNIT | Equipment - Vendor Supplied Items
| EC-4686A | L4 BATTER APPLICATOR HOLD DOWN DRUM |  | GFP-F-46-50-05 | 1 |  | VFD | PF52x | [6 empty] | 4 | L4_BATTER | LINE 4 BATTER UNIT | Equipment - Vendor Supplied Items
| EC-4687 | L4 BATTER DRIP OFF CNVR 1 |  | GFP-F-46-50-05 | 3 |  | VFD | PF52x | [6 empty] | 4 | L4_BATTER | LINE 4 BATTER UNIT | Equipment - Vendor Supplied Items
| EC-4688A | L4 BATTER DRIP OFF CNVR 2 |  | GFP-F-46-50-05 | 5 |  | VFD | PF52x | [6 empty] | 4 | L4_BATTER | LINE 4 BATTER UNIT | Equipment - Vendor Supplied Items
| EC-4689A | L4 A-STAGE FRYER FD CNVR |  | GFP-F-46-50-05 | 5 |  | VFD | PF52x | [6 empty] | 4 | L4_BATTER | LINE 4 BATTER UNIT | Equipment - Vendor Supplied Items
| EC-4690A | L4 A-STAGE FRYER FD CNVR RETRACT JACK |  | GFP-F-46-50-05 | 1.5 |  | FVR | MotorRev | [6 empty] | 4 | L4_BATTER | LINE 4 BATTER UNIT | Equipment - Vendor Supplied Items
| EC-4692A | L4 BATTER RECIRCULATION TNK SOLIDS CNVR |  | GFP-F-46-50-05 | 1 |  | VFD | PF52x | [6 empty] | 4 | L4_BATTER | LINE 4 BATTER UNIT | Equipment - Vendor Supplied Items
| EC-4693A | L4 BATTER RECIRCULATION TNK PMP |  | GFP-F-46-50-05 | 25 |  | VFD | PF52x | [6 empty] | 4 | L4_BATTER | LINE 4 BATTER UNIT | Equipment - Vendor Supplied Items
| EC-4695A | L4 BATTER BLOW OFF BLOWER 1 |  | GFP-F-46-50-05 | 20 |  | VFD | PF52x | [6 empty] | 4 | L4_BATTER | LINE 4 BATTER UNIT | Equipment - Vendor Supplied Items
| EC-4696A | L4 BATTER BLOW OFF BLOWER 2 |  | GFP-F-46-50-05 | 20 |  | VFD | PF52x | [6 empty] | 4 | L4_BATTER | LINE 4 BATTER UNIT | Equipment - Vendor Supplied Items
| EC-4705A | L4 A-STAGE FRYER CHAIN |  | GFP-F-47-50-01 | 15 |  | VFD | PF52x | [6 empty] | 4 | L4_FRYER | LINE 4 FRYER UNIT | Equipment - Vendor Supplied Items
| EC-4706A | L4 FRYER INFD HOOD BAFFLE |  | GFP-F-47-50-01 | 0.5 |  | VFD | PF52x | [6 empty] | 4 | L4_FRYER | LINE 4 FRYER UNIT | Equipment - Vendor Supplied Items
| EC-4707A | L4 FRYER HOOD JACK |  | GFP-F-47-50-01 | 7.5 |  | VFD | PF52x | [6 empty] | 4 | L4_FRYER | LINE 4 FRYER UNIT | Equipment - Vendor Supplied Items
| EC-4710A | L4 B-STAGE FRYER CHAIN |  | GFP-F-47-50-01 | 5 |  | VFD | PF52x | [6 empty] | 4 | L4_FRYER | LINE 4 FRYER UNIT | Equipment - Vendor Supplied Items
| EC-4713A | L4 FRYER DRIP PAN PMP |  | GFP-F-47-50-01 | 15 |  | VFD | PF52x | [6 empty] | 4 | L4_FRYER | LINE 4 FRYER UNIT | Equipment - Vendor Supplied Items
| EC-4714A | L4 FRYER DRIP PAN CIP PMP |  | GFP-F-47-50-01 | 5 |  | FVNR | MotorE300 | [6 empty] | 4 | L4_FRYER | LINE 4 FRYER UNIT | Equipment - Vendor Supplied Items
| EC-4717A | L4 FRYER A-STAGE ROTARY FILTER 1 |  | GFP-F-47-50-02 | 0.75 |  | FVNR | MotorE300 | [6 empty] | 4 | L4_FRYER | LINE 4 FRYER UNIT | Equipment - Vendor Supplied Items
| EC-4717B | L4 FRYER A-STAGE ROTARY FILTER 1 AUGER |  | GFP-F-47-50-02 | 0.5 |  | FVNR | MotorE300 | [6 empty] | 4 | L4_FRYER | LINE 4 FRYER UNIT | Equipment - Vendor Supplied Items
| EC-4718A | L4 FRYER A-STAGE CIRCULATION PMP 1 |  | GFP-F-47-50-02 | 200 |  | VFD | PF755 | [6 empty] | 4 | L4_FRYER | LINE 4 FRYER UNIT | Equipment - Vendor Supplied Items
| EC-4719A | L4 FRYER A-STAGE ROTARY FILTER 2 |  | GFP-F-47-50-02 | 0.75 |  | FVNR | MotorE300 | [6 empty] | 4 | L4_FRYER | LINE 4 FRYER UNIT | Equipment - Vendor Supplied Items
| EC-4719B | L4 FRYER A-STAGE ROTARY FILTER 2 AUGER |  | GFP-F-47-50-02 | 0.5 |  | FVNR | MotorE300 | [6 empty] | 4 | L4_FRYER | LINE 4 FRYER UNIT | Equipment - Vendor Supplied Items
| EC-4722A | L4 FRYER A-STAGE DRAIN PMP |  | GFP-F-47-50-02 | 15 |  | FVNR | MotorE300 | [6 empty] | 4 | L4_FRYER | LINE 4 FRYER UNIT | Equipment - Vendor Supplied Items
| EC-4724A | L4 DRAIN TNK PMP |  | GFP-F-47-50-02 | 7.5 |  | VFD | PF52x | [6 empty] | 4 | L4_FRYER | LINE 4 FRYER UNIT | Equipment - Vendor Supplied Items
| EC-4727A | L4 FRYER OIL MAKEUP PMP |  | GFP-F-47-50-02 | 7.5 |  | VFD | PF52x | [6 empty] | 4 | L4_FRYER | LINE 4 FRYER UNIT | Equipment-Relocated
| EC-4728A | L4 FRYER FAST FILL PMP |  | GFP-F-47-50-02 | 5 |  | VFD | PF52x | [6 empty] | 4 | L4_FRYER | LINE 4 FRYER UNIT | Equipment-Relocated
| EC-4736A | L4 A-STAGE FRYER OBERLIN FD PMP |  | GFP-F-47-50-03 | 2 |  | VFD | PF52x | [6 empty] | 4 | L4_FRYER | LINE 4 FRYER UNIT | PID
| EC-4739A | L4 A-STAGE OBERLIN CLEAN OIL PMP |  | GFP-F-47-50-06 | 7.5 |  | VFD | PF52x | [6 empty] | 4 | L4_FRYER | LINE 4 FRYER UNIT | Equipment - Vendor Supplied Items
| EC-4747A | L4 FRYER B-STAGE ROTARY FILTER 1 |  | GFP-F-47-50-04 | 0.75 |  | FVNR | MotorE300 | [6 empty] | 4 | L4_FRYER | LINE 4 FRYER UNIT | Equipment - Vendor Supplied Items
| EC-4747B | L4 FRYER B-STAGE ROTARY FILTER 1 AUGER |  | GFP-F-47-50-04 | 0.5 |  | FVNR | MotorE300 | [6 empty] | 4 | L4_FRYER | LINE 4 FRYER UNIT | Equipment - Vendor Supplied Items
| EC-4748A | L4 FRYER B-STAGE CIRCULATION PMP |  | GFP-F-47-50-04 | 200 |  | VFD | PF755 | [6 empty] | 4 | L4_FRYER | LINE 4 FRYER UNIT | Equipment - Vendor Supplied Items
| EC-4749A | L4 FRYER B-STAGE ROTARY FILTER 2 |  | GFP-F-47-50-04 | 0.75 |  | FVNR | MotorE300 | [6 empty] | 4 | L4_FRYER | LINE 4 FRYER UNIT | Equipment - Vendor Supplied Items
| EC-4749B | L4 FRYER B-STAGE ROTARY FILTER 2 AUGER |  | GFP-F-47-50-04 | 0.5 |  | FVNR | MotorE300 | [6 empty] | 4 | L4_FRYER | LINE 4 FRYER UNIT | Equipment - Vendor Supplied Items
| EC-4753A | L4 FRYER B-STAGE DRAIN PMP |  | GFP-F-47-50-04 | 15 |  | FVNR | MotorE300 | [6 empty] | 4 | L4_FRYER | LINE 4 FRYER UNIT | Equipment - Vendor Supplied Items
| EC-4755A | L4 FRYER CRUMB COLL AUGER |  | GFP-F-47-50-04 | 1 |  | FVNR | MotorE300 | [6 empty] | 4 | L4_FRYER | LINE 4 FRYER UNIT | PID
| EC-4757A | L4 FRYER CRUMB PRESS FD AUGER |  | GFP-F-47-50-04 | 1 |  | FVNR | MotorE300 | [6 empty] | 4 | L4_FRYER | LINE 4 FRYER UNIT | PID
| EC-4758A | L4 FRYER CRUMB PRESS |  | GFP-F-47-50-04 | 10 |  | VFD | PF52x | [6 empty] | 4 | L4_FRYER | LINE 4 FRYER UNIT | Equipment - Vendor Supplied Items
| EC-4759A | L4 FRYER CRUMB PRESS PMP |  | GFP-F-47-50-04 | 1.5 |  | VFD | PF52x | [6 empty] | 4 | L4_FRYER | LINE 4 FRYER UNIT | Equipment - Vendor Supplied Items
| EC-4771A | L4 B-STAGE FRYER OBERLIN FD PMP |  | GFP-F-47-50-05 | 2 |  | VFD | PF52x | [6 empty] | 4 | L4_FRYER | LINE 4 FRYER UNIT | PID
| EC-4774A | L4 B-STAGE OBERLIN CLEAN OIL PMP |  | GFP-F-47-50-07 | 7.5 |  | VFD | PF52x | [6 empty] | 4 | L4_FRYER | LINE 4 FRYER UNIT | Equipment - Vendor Supplied Items
| EC-4783A | L4 FRYER EXHAUST FAN |  | GFP-F-47-50-08 | 30 |  | VFD | PF755 | [6 empty] | 4 | L4_FRYER | LINE 4 FRYER UNIT | Equipment - Vendor Supplied Items
| EC-4784A | L4 MISC FRYER EQUIPMENT EXHAUST FAN |  | GFP-F-47-50-08 | 5 |  | VFD | PF52x | [6 empty] | 4 | L4_FRYER | LINE 4 FRYER UNIT | PID
| EC-4785A | L4 OIL MISER CNVR |  | GFP-F-47-50-09 | 5 |  | VFD | PF52x | [6 empty] | 4 | L4_FRYER | LINE 4 FRYER UNIT | Equipment - Vendor Supplied Items
| EC-4785B | L4 OIL MISER CNVR |  | GFP-F-47-50-09 | 1 |  | VFD | PF52x | [6 empty] | 4 | L4_FRYER | LINE 4 FRYER UNIT | Equipment - Vendor Supplied Items
| EC-4786A | L4 OIL MISER CYCLONES ROTARY VALVE 1 |  | GFP-F-47-50-09 | 0.5 |  | VFD | PF52x | [6 empty] | 4 | L4_FRYER | LINE 4 FRYER UNIT | Equipment - Vendor Supplied Items
| EC-4786B | L4 OIL MISER CYCLONES ROTARY VALVE 2 |  | GFP-F-47-50-09 | 0.5 |  | VFD | PF52x | [6 empty] | 4 | L4_FRYER | LINE 4 FRYER UNIT | Equipment - Vendor Supplied Items
| EC-4786C | L4 OIL MISER CYCLONES ROTARY VALVE 3 |  | GFP-F-47-50-09 | 0.5 |  | VFD | PF52x | [6 empty] | 4 | L4_FRYER | LINE 4 FRYER UNIT | Equipment - Vendor Supplied Items
| EC-4786D | L4 OIL MISER CYCLONES ROTARY VALVE 4 |  | GFP-F-47-50-09 | 0.5 |  | VFD | PF52x | [6 empty] | 4 | L4_FRYER | LINE 4 FRYER UNIT | Equipment - Vendor Supplied Items
| EC-4794A | L4 OIL MISER FAN |  | GFP-F-47-50-09 | 150 |  | VFD | PF755 | [6 empty] | 4 | L4_FRYER | LINE 4 FRYER UNIT | Equipment - Vendor Supplied Items
| EC-4793A | L4 OIL MISER RETURN PMP |  | GFP-F-47-50-09 | 3 |  | VFD | PF52x | [6 empty] | 4 | L4_FRYER | LINE 4 FRYER UNIT | Equipment - Vendor Supplied Items
| EC-4795A | L4 PRECOOL FD SHKR |  | GFP-F-47-50-09 | 3 |  | FVNR | MotorE300 | [6 empty] | 4 | L4_FRYER | LINE 4 FRYER UNIT | Equipment - Vendor Supplied Items
| EC-4803A | L4 FREEZE TUNNEL BELT DRYER-1 |  | GFP-F-48-50-01 | 10 |  | FVNR | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-4804A | L4 FREEZE TUNNEL BELT DRYER-2 |  | GFP-F-48-50-01 | 10 |  | FVNR | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-4805A | L4 REFRIGERATED PRECOOL BELT |  | GFP-F-48-50-01 | 5 |  | VFD | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-4806A | L4 FREEZE TUNNEL FAN-01 |  | GFP-F-48-50-01 | 30 |  | VFD | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-4807A | L4 FREEZE TUNNEL FAN-02 |  | GFP-F-48-50-01 | 30 |  | VFD | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-4808A | L4 FREEZE TUNNEL FAN-03 |  | GFP-F-48-50-01 | 30 |  | VFD | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-4809A | L4 FREEZE TUNNEL FAN-04 |  | GFP-F-48-50-01 | 30 |  | VFD | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-4810A | L4 FREEZE TUNNEL FAN-05 |  | GFP-F-48-50-01 | 30 |  | VFD | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-4815A | L4 FREEZE TUNNEL BELT VIBRATOR-01 |  | GFP-F-48-50-01 | 3 |  | FVNR | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-4816A | L4 FREEZE TUNNEL BELT VIBRATOR-02 |  | GFP-F-48-50-01 | 3 |  | FVNR | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-4817A | L4 FREEZE TUNNEL BELT VIBRATOR-03 |  | GFP-F-48-50-01 | 3 |  | FVNR | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-4818A | L4 FREEZE TUNNEL BELT VIBRATOR-04 |  | GFP-F-48-50-01 | 3 |  | FVNR | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-4821A | L4 PRECOOL CIP RETURN PMP |  | GFP-F-48-50-01 | 20 |  | VFD | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-4825A | L4 FREEZE TUNNEL |  | GFP-F-48-50-03 | 7.5 |  | VFD | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-4826A | L4 FREEZE TUNNEL FAN-06 |  | GFP-F-48-50-02 | 30 |  | VFD | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-4827 | 5 FREEZE TUNNEL FAN-07 |  | GFP-F-48-50-02 | 30 |  | VFD | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-4828 | L4 FREEZE TUNNEL FAN-08 |  | GFP-F-48-50-02 | 30 |  | VFD | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-4829 | L4 FREEZE TUNNEL FAN-9 |  | GFP-F-48-50-02 | 30 |  | VFD | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-4830 | L4 FREEZE TUNNEL FAN-10 |  | GFP-F-48-50-02 | 30 |  | VFD | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-4831A | L4 FREEZE TUNNEL FAN-11 |  | GFP-F-48-50-03 | 30 |  | VFD | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-4832A | L4 FREEZE TUNNEL FAN-12 |  | GFP-F-48-50-03 | 30 |  | VFD | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-4833A | L4 FREEZE TUNNEL FAN-13 |  | GFP-F-48-50-03 | 30 |  | VFD | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-4834A | L4 FREEZE TUNNEL FAN-14 |  | GFP-F-48-50-03 | 30 |  | VFD | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-4835A | L4 FREEZE TUNNEL FAN-15 |  | GFP-F-48-50-03 | 30 |  | VFD | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-4836A | L4 FREEZE TUNNEL FAN-16 |  | GFP-F-48-50-03 | 30 |  | VFD | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-4842A | L4 FREEZE TUNNEL BELT VIBRATOR-09 |  | GFP-F-48-50-03 | 3 |  | FVNR | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-4843A | L4 FREEZE TUNNEL BELT VIBRATOR-10 |  | GFP-F-48-50-03 | 3 |  | FVNR | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-4845A | L4 FREEZE TUNNEL BELT VIBRATOR-05 |  | GFP-F-48-50-02 | 3 |  | FVNR | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-4846A | L4 FREEZE TUNNEL BELT VIBRATOR-06 |  | GFP-F-48-50-02 | 3 |  | FVNR | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-4847A | L4 FREEZE TUNNEL BELT VIBRATOR-07 |  | GFP-F-48-50-02 | 3 |  | FVNR | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-4848A | L4 FREEZE TUNNEL BELT VIBRATOR-08 |  | GFP-F-48-50-02 | 3 |  | FVNR | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-4851A | L4 FREEZE TUNNEL CIP RETURN PMP |  | GFP-F-48-50-03 | 20 |  | VFD | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-4855A | L4 FREEZE TUNNEL AIR BALANCE FAN 1 |  | GFP-F-48-50-03 | 3 |  | VFD | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-4860A | L4 FREEZE TUNNEL SUMP PMP |  | GFP-F-48-50-03 | ? |  | VFD | PF52x | [6 empty] | 4 | L4_SUMP | LINE 4 SUMP UNIT | Question
| EC-4902A | L4 FREEZE TUNNEL DISCH SHKR |  | GFP-F-49-50-01 | 3 |  | FVNR | MotorE300 | [6 empty] | 4 | L4_TOTE | LINE 4 TOTE OFF UNIT | Equipment - Vendor Supplied Items
| EC-4904A | L4 FREEZER TRANSFER CNVR 1 |  | GFP-F-49-50-01 | 5 |  | FVNR | MotorE300 | [6 empty] | 4 | L4_TOTE | LINE 4 TOTE OFF UNIT | Equipment - Vendor Supplied Items
| EC-4906A | L4 FREEZER TRANSFER CNVR 2 |  | GFP-F-49-50-01 | 5 |  | VFD | PF52x | [6 empty] | 4 | L4_TOTE | LINE 4 TOTE OFF UNIT | Equipment - Vendor Supplied Items
| EC-4910A | L4 TOTE-OFF SHKR 1 |  | GFP-F-49-50-01 | 4.8 |  | FVNR | MotorE300 | [6 empty] | 4 | L4_TOTE | LINE 4 TOTE OFF UNIT | Equipment - Vendor Supplied Items
| EC-4912A | L4 TOTE-OFF SHKR 2 |  | GFP-F-49-50-01 | 4.8 |  | FVNR | MotorE300 | [6 empty] | 4 | L4_TOTE | LINE 4 TOTE OFF UNIT | Equipment - Vendor Supplied Items
| EC-4914A | L4 FREEZER TRANSFER CNVR 3 |  | GFP-F-49-50-01 | 5 |  | FVNR | MotorE300 | [6 empty] | 4 | L4_TOTE | LINE 4 TOTE OFF UNIT | Equipment - Vendor Supplied Items
| EC-4915A | L4 FROZEN GRADING FD WEIGH BELT |  | GFP-F-49-50-01 | 5 |  | FVNR | MotorE300 | [6 empty] | 4 | L4_TOTE | LINE 4 TOTE OFF UNIT | PID
| EC-4925A | L4 ADD BACK TOTE DUMP |  | GFP-F-49-50-01 | ? |  | VFD | PF52x | [6 empty] | 4 | L4_TOTE | LINE 4 TOTE OFF UNIT | Equipment-Modified
| EC-4927A | L4 ADD BACK INCLINE CNVR |  | GFP-F-49-50-01 | ? |  | VFD | PF52x | [6 empty] | 4 | L4_TOTE | LINE 4 TOTE OFF UNIT | Question
| EC-7470A | L4 PRECOOL CIP SKID |  | GFP-F-74-50-02 | 1 |  | VFD | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-7471 | L4 PRECOOL CIP TNK SKID PMP |  | GFP-F-74-50-02 | 40 |  | FVNR | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-7475A | L4 FREEZE TUNNEL CIP SKID |  | GFP-F-74-50-03 | 1 |  | VFD | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-7476A | L4 FREEZE TUNNEL CIP SKID PMP |  | GFP-F-74-50-03 | 40 |  | FVNR | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-7481A | L4 DRYER CIP SKID PMP |  | GFP-F-74-50-01 | 40 |  | VFD | OEM | [6 empty] | 4 | L4_DRYER | LINE 4 DRYER UNIT | Equipment - Vendor Supplied Items
| EC-7908A | PLANT WASTE TOTE DUMP HYDRAULIC PMP |  | GFP-F-79-50-01 | 10 |  | FVNR | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-7910A | PLANT WASTE TOTE DUMP AUGER |  | GFP-F-79-50-01 | 5 |  | FVNR | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-9505A | WESP RECYCLE PMP |  | GFP-F-95-50-02 | 15 |  |  | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items
| EC-9507A | WESP FLUSH PMP |  | GFP-F-95-50-03 | 15 |  |  | OEM | [6 empty] | 4 | OEM |  | Equipment - Vendor Supplied Items

## Instrument List
REVISION | REVISION DATE | FULL ID | TYPE | Equipment Number | TAG | DESCRIPTION | CONNECTION | SIGNAL TYPE | WIRED TO | SUPPLIED BY | INSTALLED BY | WIRED BY | MOUNT TYPE | MOUNT SUPPLIED BY | INSTRUMENT MFR | INSTRUMENT PN | MOUNT MFR | MOUNT PN | PID DRAWING | PID LAYER | LINE | UNIT | Control Type | UNIT DESC | Status | ASi Master
|  | HS-4685A | HS | 4685 | 4685A | L4 BTTR APP E-STOP | 4-WIRE | DI | ? | ? | [8 empty] | GFP-F-46-50-05 | PID | 4 | L4_BATTER | DIn | LINE 4 BATTER UNIT
|  | HS-4685B | HS | 4685 | 4685B | L4 BTTR APP E-STOP | 4-WIRE | DI | ? | ? | [8 empty] | GFP-F-46-50-05 | PID | 4 | L4_BATTER | DIn | LINE 4 BATTER UNIT
|  | XV-4670A | XV | 4670 | 4670A | L4 BTTR HEX VLV | AS-I | DI/DO | ? | ? | [8 empty] | GFP-F-46-50-04 | PID | 4 | L4_BATTER | ValveSO | LINE 4 BATTER UNIT
|  | XV-4084A | XV | 4084 | 4084A | L4 PEF FD RETURN WTR TNK COLD WTR VLV | AS-I | DI/DO | L04PRC-R1 | Others | [8 empty] | GFP-F-40-50-02-New | PID | 4 | L4_PEF | ValveSO | LINE 4 PEF UNIT |  | L04PRC-R1-ASM01
|  | XV-4084B | XV | 4084 | 4084B | L4 PEF FD RETURN WTR TNK DRN VLV | AS-I | DI/DO | L04PRC-R1 | ? | [8 empty] | GFP-F-40-50-02-New | PID | 4 | L4_PEF | ValveSO | LINE 4 PEF UNIT |  | L04PRC-R1-ASM01
|  | XV-4090A | XV | 4090 | 4090A | L4 PEF CIP PMP CIP DRN VLV | AS-I | DI/DO | L04PRC-R1 | Others | [8 empty] | GFP-F-40-50-02-New | PID | 4 | L4_PEF | ValveSO | LINE 4 PEF UNIT |  | L04PRC-R1-ASM01
|  | XV-4460A | XV | 4460 | 4460A | L4 SAPP PRODUCT TNK HOT WTR VLV | AS-I | DI/DO | L04PRC-R1 | Others | [8 empty] | GFP-F-44-50-01-New | PID | 4 | L4_SAPP | ValveSO | LINE 4 SAPP UNIT |  | L04PRC-R1-ASM01
|  | XV-4505A | XV | 4505 | 4505A | L4 DRYER STAGE A COLD WTR VLV | AS-I | DI/DO | L04PRC-R1 | RJX | [8 empty] | GFP-F-45-50-01 | PID | 4 | L4_DRYER | ValveSO | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | XV-4505B | XV | 4505 | 4505B | L4 DRYER STAGE A CIP VLV | AS-I | DI/DO | L04PRC-R1 | RJX | [8 empty] | GFP-F-45-50-01 | PID | 4 | L4_DRYER | ValveSO | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | XV-4506A | XV | 4506 | 4506A | L4 DRYER STAGE A CIP VLV | AS-I | DI/DO | L04PRC-R1 | RJX | [8 empty] | GFP-F-45-50-01 | PID | 4 | L4_DRYER | ValveSO | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | XV-4506B | XV | 4506 | 4506B | L4 DRYER STAGE A CIP VLV | AS-I | DI/DO | L04PRC-R1 | RJX | [8 empty] | GFP-F-45-50-01 | PID | 4 | L4_DRYER | ValveSO | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | XV-4535A | XV | 4535 | 4535A | L4 DRYER STAGE B CIP VLV | AS-I | DI/DO | L04PRC-R1 | RJX | [8 empty] | GFP-F-45-50-02 | PID | 4 | L4_DRYER | ValveSO | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | XV-4535B | XV | 4535 | 4535B | L4 DRYER STAGE B CIP VLV | AS-I | DI/DO | L04PRC-R1 | RJX | [8 empty] | GFP-F-45-50-02 | PID | 4 | L4_DRYER | ValveSO | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | XV-4536A | XV | 4536 | 4536A | L4 DRYER STAGE B CIP VLV | AS-I | DI/DO | L04PRC-R1 | RJX | [8 empty] | GFP-F-45-50-02 | PID | 4 | L4_DRYER | ValveSO | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | XV-4536B | XV | 4536 | 4536B | L4 DRYER STAGE B CIP VLV | AS-I | DI/DO | L04PRC-R1 | RJX | [8 empty] | GFP-F-45-50-02 | PID | 4 | L4_DRYER | ValveSO | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | XV-4565A | XV | 4565 | 4565A | L4 DRYER CIP RETURN PMP DRN VLV | AS-I | DI/DO | L04PRC-R1 | RJX | [8 empty] | GFP-F-45-50-02 | PID | 4 | L4_DRYER | ValveSO | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | XV-4082A | XV | 4082 | 4082A | L4 PEF FD DEWTRING SHKR ABORT GATE | 3-WIRE | DO | L04PRC-R1-JB01 | OEM | [8 empty] | GFP-F-40-50-02-New | PID | 4 | L4_PEF | ValveSO | LINE 4 PEF UNIT |  | L04PRC-R1-ASM01
|  | LIT-4084A | LIT | 4084 | 4084A | L4 PEF FD RETURN WTR TNK LVL | 4-WIRE | AI | L04PRC-R1-JB02 | OEM | [8 empty] | GFP-F-40-50-02-New | PID | 4 | L4_PEF | AIn | LINE 4 PEF UNIT |  | L04PRC-R1-ASM01
|  | FS-4090A | FS | 4090 | 4090A | L4 PEF CIP PMP FLOW | 3-WIRE | DI | L04PRC-R1-JB02 | RJX | [8 empty] | GFP-F-40-50-02-New | PID | 4 | L4_PEF | DIn | LINE 4 PEF UNIT |  | L04PRC-R1-ASM01
|  | SV-5677A | SV | 5677 | 5677A | L4 PEF CAUSTIC PMP AIR VLV | 3-WIRE | RLY | L04PRC-R1-JB02 | Others | [8 empty] | GFP-F-40-50-02-New | PID | 4 | L4_PEF | DOut | LINE 4 PEF UNIT |  | L04PRC-R1-ASM01
|  | LIT-4460A | LIT | 4460 | 4460A | L4 SAPP PRODUCT TNK LVL | 4-WIRE | AI | L04PRC-R1-JB03 | OEM | [8 empty] | GFP-F-44-50-01-New | PID | 4 | L4_SAPP | AIn | LINE 4 SAPP UNIT |  | L04PRC-R1-ASM01
|  | LIT-4505A | LIT | 4505 | 4505A | L4 DRYER STAGE A LVL | 4-WIRE | AI | L04PRC-R1-JB04 | RJX | [8 empty] | GFP-F-45-50-01 | PID | 4 | L4_DRYER | AIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | TT-4505A | TT | 4505 | 4505A | L4 DRYER STAGE A TEMP | 4-WIRE | AI | L04PRC-R1-JB05 | RJX | [8 empty] | GFP-F-45-50-01 | PID | 4 | L4_DRYER | AIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | TT-4505C | TT | 4505 | 4505C | L4 DRYER STAGE A TEMP | 4-WIRE | AI | L04PRC-R1-JB05 | RJX | [8 empty] | GFP-F-45-50-01 | PID | 4 | L4_DRYER | AIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | LIT-4530A | LIT | 4530 | 4530A | L4 DRYER CIP FLUME LVL | 4-WIRE | AI | L04PRC-R1-JB05 | RJX | [8 empty] | GFP-F-45-50-02 | PID | 4 | L4_DRYER | AIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | TT-4535A | TT | 4535 | 4535A | L4 DRYER STAGE B TEMP | 4-WIRE | AI | L04PRC-R1-JB05 | RJX | [8 empty] | GFP-F-45-50-02 | PID | 4 | L4_DRYER | AIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | TT-4535C | TT | 4535 | 4535C | L4 DRYER STAGE B TEMP | 4-WIRE | AI | L04PRC-R1-JB05 | RJX | [8 empty] | GFP-F-45-50-02 | PID | 4 | L4_DRYER | AIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | LSL-4505A | LSL | 4505 | 4505A | L4 DRYER STAGE A LVL LOW | 3-WIRE | DI | L04PRC-R1-JB05 | OEM | [8 empty] | GFP-F-45-50-01 | PID | 4 | L4_DRYER | DIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | ZS-4505A | ZS | 4505 | 4505A | L4 DRYER STAGE A POS | 3-WIRE | DI | L04PRC-R1-JB05 | OEM | [8 empty] | GFP-F-45-50-01 | Equipment - Vendor Supplied Items | 4 | L4_DRYER | DIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | ZS-4505B | ZS | 4505 | 4505B | L4 DRYER STAGE A POS | 3-WIRE | DI | L04PRC-R1-JB05 | RJX | [8 empty] | GFP-F-45-50-01 | PID | 4 | L4_DRYER | DIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | LSL-4535A | LSL | 4535 | 4535A | L4 DRYER STAGE B LVL LOW | 3-WIRE | DI | L04PRC-R1-JB05 | OEM | [8 empty] | GFP-F-45-50-02 | PID | 4 | L4_DRYER | DIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | ZS-4535B | ZS | 4535 | 4535B | L4 DRYER STAGE B POS | 3-WIRE | DI | L04PRC-R1-JB05 | RJX | [8 empty] | GFP-F-45-50-02 | Equipment - Vendor Supplied Items | 4 | L4_DRYER | DIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | ZS-4535G | ZS | 4535 | 4535G | L4 DRYER STAGE B POS | 3-WIRE | DI | L04PRC-R1-JB05 | OEM | [8 empty] | GFP-F-45-50-02 | PID | 4 | L4_DRYER | DIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | SV-4505B | SV | 4505 | 4505B | L4 DRYER STAGE A OILER VLV | 3-WIRE | DO | L04PRC-R1-JB05 | RJX | [8 empty] | GFP-F-45-50-01 | PID | 4 | L4_DRYER | DOut | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | SV-4535B | SV | 4535 | 4535B | L4 DRYER STAGE B OILER VLV | 3-WIRE | DO | L04PRC-R1-JB05 | RJX | [8 empty] | GFP-F-45-50-02 | PID | 4 | L4_DRYER | DOut | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | TT-4505B | TT | 4505 | 4505B | L4 DRYER STAGE A TEMP | 4-WIRE | AI | L04PRC-R1-JB06 | RJX | [8 empty] | GFP-F-45-50-01 | PID | 4 | L4_DRYER | AIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | TT-4505D | TT | 4505 | 4505D | L4 DRYER STAGE A TEMP | 4-WIRE | AI | L04PRC-R1-JB06 | RJX | [8 empty] | GFP-F-45-50-01 | PID | 4 | L4_DRYER | AIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | HIT-4518A | HIT | 4518 | 4518A | L4 DRYER ZONE 1 EXHST HUMIDITY | 4-WIRE | AI | L04PRC-R1-JB06 | RJX | [8 empty] | GFP-F-45-50-01 | PID | 4 | L4_DRYER | AIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | HIT-4528A | HIT | 4528 | 4528A | L4 DRYER ZONE 2 EXHST HUMIDITY | 4-WIRE | AI | L04PRC-R1-JB06 | RJX | [8 empty] | GFP-F-45-50-01 | PID | 4 | L4_DRYER | AIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | TT-4535B | TT | 4535 | 4535B | L4 DRYER STAGE B TEMP | 4-WIRE | AI | L04PRC-R1-JB06 | RJX | [8 empty] | GFP-F-45-50-02 | PID | 4 | L4_DRYER | AIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | TT-4535D | TT | 4535 | 4535D | L4 DRYER STAGE B TEMP | 4-WIRE | AI | L04PRC-R1-JB06 | RJX | [8 empty] | GFP-F-45-50-02 | PID | 4 | L4_DRYER | AIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | HIT-4548A | HIT | 4548 | 4548A | L4 DRYER ZONE 3 EXHST HUMIDITY | 4-WIRE | AI | L04PRC-R1-JB06 | RJX | [8 empty] | GFP-F-45-50-02 | PID | 4 | L4_DRYER | AIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | HIT-4558A | HIT | 4558 | 4558A | L4 DRYER ZONE 2 EXHST HUMIDITY | 4-WIRE | AI | L04PRC-R1-JB06 | RJX | [8 empty] | GFP-F-45-50-01 | PID | 4 | L4_DRYER | AIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | TSH-4505A | TSH | 4505 | 4505A | L4 DRYER STAGE A TEMP HI | 3-WIRE | DI | L04PRC-R1-JB06 | RJX | [8 empty] | GFP-F-45-50-01 | PID | 4 | L4_DRYER | DIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | TSH-4505B | TSH | 4505 | 4505B | L4 DRYER STAGE A TEMP HI | 3-WIRE | DI | L04PRC-R1-JB06 | RJX | [8 empty] | GFP-F-45-50-01 | PID | 4 | L4_DRYER | DIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | PSL-4510A | PSL | 4510 | 4510A | L4 DRYER ZONE 1 RECIRC FAN 1 PRESS LOW | 3-WIRE | DI | L04PRC-R1-JB06 | RJX | [8 empty] | GFP-F-45-50-01 | PID | 4 | L4_DRYER | DIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | PSL-4518A | PSL | 4518 | 4518A | L4 DRYER ZONE 1 EXHST FAN PRESS LOW | 3-WIRE | DI | L04PRC-R1-JB06 | RJX | [8 empty] | GFP-F-45-50-01 | PID | 4 | L4_DRYER | DIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | TSH-4518A | TSH | 4518 | 4518A | L4 DRYER ZONE 1 EXHST FAN TEMP HI | 3-WIRE | DI | L04PRC-R1-JB06 | RJX | [8 empty] | GFP-F-45-50-01 | PID | 4 | L4_DRYER | DIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | PSL-4520A | PSL | 4520 | 4520A | L4 DRYER ZONE 2 RECIRC FAN 1 PRESS LOW | 3-WIRE | DI | L04PRC-R1-JB06 | RJX | [8 empty] | GFP-F-45-50-01 | PID | 4 | L4_DRYER | DIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | PSL-4528A | PSL | 4528 | 4528A | L4 DRYER ZONE 2 EXHST FAN PRESS LOW | 3-WIRE | DI | L04PRC-R1-JB06 | RJX | [8 empty] | GFP-F-45-50-01 | PID | 4 | L4_DRYER | DIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | TSH-4528A | TSH | 4528 | 4528A | L4 DRYER ZONE 2 EXHST FAN TEMP HI | 3-WIRE | DI | L04PRC-R1-JB06 | RJX | [8 empty] | GFP-F-45-50-01 | PID | 4 | L4_DRYER | DIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | TSH-4535A | TSH | 4535 | 4535A | L4 DRYER STAGE B TEMP HI | 3-WIRE | DI | L04PRC-R1-JB06 | RJX | [8 empty] | GFP-F-45-50-02 | PID | 4 | L4_DRYER | DIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | TSH-4535B | TSH | 4535 | 4535B | L4 DRYER STAGE B TEMP HI | 3-WIRE | DI | L04PRC-R1-JB06 | RJX | [8 empty] | GFP-F-45-50-02 | PID | 4 | L4_DRYER | DIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | PSL-4540A | PSL | 4540 | 4540A | L4 DRYER ZONE 3 RECIRC FAN 1 PRESS LOW | 3-WIRE | DI | L04PRC-R1-JB06 | RJX | [8 empty] | GFP-F-45-50-02 | PID | 4 | L4_DRYER | DIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | PSL-4548A | PSL | 4548 | 4548A | L4 DRYER ZONE 3 EXHST FAN PRESS LOW | 3-WIRE | DI | L04PRC-R1-JB06 | RJX | [8 empty] | GFP-F-45-50-02 | PID | 4 | L4_DRYER | DIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | TSH-4548A | TSH | 4548 | 4548A | L4 DRYER ZONE 3 EXHST FAN TEMP HI | 3-WIRE | DI | L04PRC-R1-JB06 | RJX | [8 empty] | GFP-F-45-50-02 | PID | 4 | L4_DRYER | DIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | PSL-4550A | PSL | 4550 | 4550A | L4 DRYER ZONE 4 RECIRC FAN 1 PRESS LOW | 3-WIRE | DI | L04PRC-R1-JB06 | RJX | [8 empty] | GFP-F-45-50-02 | PID | 4 | L4_DRYER | DIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | PSL-4558A | PSL | 4558 | 4558A | L4 DRYER ZONE 4 EXHST FAN PRESS LOW | 3-WIRE | DI | L04PRC-R1-JB06 | RJX | [8 empty] | GFP-F-45-50-02 | PID | 4 | L4_DRYER | DIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | TSH-4558A | TSH | 4558 | 4558A | L4 DRYER ZONE 4 EXHST FAN TEMP HI | 3-WIRE | DI | L04PRC-R1-JB06 | RJX | [8 empty] | GFP-F-45-50-02 | PID | 4 | L4_DRYER | DIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | LIT-4568A | LIT | 4568 | 4568A | L5 DRYER DISCH SHKR LVL | 4-WIRE | AI | L04PRC-R1-JB07 | RJX | [8 empty] | GFP-F-45-50-02 | PID | 4 | L4_DRYER | AIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | TT-7480B | TT | 7480 | 7480B | L4 DRYER CIP SKID TEMP | 4-WIRE | AI | L04PRC-R1-JB07 | RJX | [8 empty] | GFP-F-48-50-03 | PID | 4 | L4_DRYER | AIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | PT-7481B | PT | 7481 | 7481B | L4 DRYER CIP SKID DSCH PRESS 2 | 4-WIRE | AI | L04PRC-R1-JB07 | OEM | [8 empty] | GFP-F-48-50-03 | PID | 4 | L4_DRYER | AIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | PT-7481A | PT | 7481 | 7481A | L4 DRYER CIP SKID DSCH PRESS 1 | 4-WIRE | AI | L04PRC-R1-JB07 | OEM | [8 empty] | GFP-F-48-50-03 | PID | 4 | L4_DRYER | AIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | FS-7480A | FS | 7480 | 7480A | L4 DRYER CIP SKID FLOW SWTCH | 3-WIRE | DI | L04PRC-R1-JB07 | RJX | [8 empty] | GFP-F-48-50-03 | PID | 4 | L4_DRYER | DIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | CIT-7480A | CIT | 7480 | 7480A | L4 DRYER CIP SKID COND | OEM | OEM | L04PRC-R1-JB07 | OEM | [8 empty] | GFP-F-48-50-03 | PID | 4 | L4_DRYER | AIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | LIT-7480A | LIT | 7480 | 7480A | L4 DRYER CIP SKID LVL | OEM | OEM | L04PRC-R1-JB07 | OEM | [8 empty] | GFP-F-48-50-03 | PID | 4 | L4_DRYER | AIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | TT-7480A | TT | 7480 | 7480A | L4 DRYER CIP SKID TEMP | OEM | OEM | L04PRC-R1-JB07 | OEM | [8 empty] | GFP-F-48-50-03 | PID | 4 | L4_DRYER | AIn | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | SV-4568A | SV | 4568 | 4568A | L5 DRYER DISCH SHKR ABORT GATE | 3-WIRE | DO | L04PRC-R1-JB08 | OEM | [8 empty] | GFP-F-45-50-02 | Equipment - Vendor Supplied Items | 4 | L4_DRYER | DOut | LINE 4 DRYER UNIT |  | L04PRC-R1-ASM01
|  | XV-4666A | XV | 4666 | 4666A | L4 BTTR HOLDING TNK PMP DRN VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-46-50-04 | PID | 4 | L4_BATTER | ValveSO | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | XV-4670C | XV | 4670 | 4670C | L4 BTTR HEX RECIRC VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-46-50-04 | Equipment - Vendor Supplied Items | 4 | L4_BATTER | ValveSO | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | XV-4670D | XV | 4670 | 4670D | L4 BTTR HEX AIR VLV | AS-I | DI/DO | L04PRC-R2 | Others | [8 empty] | GFP-F-46-50-04 | PID | 4 | L4_BATTER | ValveSO | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | XV-4665B | XV | 4665 | 4665B | L4 BTTR HOLDING TNK HOT WTR VLV | AS-I | DI/DO | L04PRC-R2 | Others | [8 empty] | GFP-F-46-50-04 | PID | 4 | L4_BATTER | ValveSO | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | XV-4665D | XV | 4665 | 4665D | L4 BTTR HOLDING TNK GLYCOL VLV | AS-I | DI/DO | L04PRC-R2 | Others | [8 empty] | GFP-F-46-50-04 | PID | 4 | L4_BATTER | ValveSO | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | XV-4665E | XV | 4665 | 4665E | L4 BTTR HOLDING TNK CIP VLV | AS-I | DI/DO | L04PRC-R2 | Others | [8 empty] | GFP-F-46-50-04 | PID | 4 | L4_BATTER | D4SDTag | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | XV-4685B | XV | 4685 | 4685B | L4 BTTR APP GLYCOL VLV | AS-I | DI/DO | L04PRC-R2 | Others | [8 empty] | GFP-F-46-50-05 | PID | 4 | L4_BATTER | ValveSO | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | XV-4685C | XV | 4685 | 4685C | L4 BTTR APP COLD WTR VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-46-50-05 | PID | 4 | L4_BATTER | ValveSO | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | XV-4689A | XV | 4689 | 4689A | L4 A-STAGE FRYER FD CNVR DRN VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-46-50-05 | PID | 4 | L4_BATTER | ValveSO | LINE 4 BATTER UNIT |  | L04PRC-R3-ASM01
|  | XV-4692B | XV | 4692 | 4692B | L4 BTTR RECIRC TNK HOT WTR VLV | AS-I | DI/DO | L04PRC-R2 | Others | [8 empty] | GFP-F-46-50-05 | PID | 4 | L4_BATTER | ValveSO | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | XV-4693A | XV | 4693 | 4693A | L4 BTTR RECIRC TNK PMP DRN VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-46-50-05 | PID | 4 | L4_BATTER | ValveSO | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | XV-4693B | XV | 4693 | 4693B | L4 BTTR RECIRC TNK PMP RECIRC VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-46-50-05 | PID | 4 | L4_BATTER | D4SDTag | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | XV-4693C | XV | 4693 | 4693C | L4 BTTR RECIRC TNK PMP CIP VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-46-50-05 | PID | 4 | L4_BATTER | ValveSO | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | XV-4693D | XV | 4693 | 4693D | L4 BTTR RECIRC TNK PMP CIP VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-46-50-05 | PID | 4 | L4_BATTER | ValveSO | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | XV-4693E | XV | 4693 | 4693E | L4 BTTR RECIRC TNK PMP CIP VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-46-50-05 | Equipment - Vendor Supplied Items | 4 | L4_BATTER | ValveSO | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | XV-4693F | XV | 4693 | 4693F | L4 BTTR RECIRC TNK PMP CIP VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-46-50-05 | PID | 4 | L4_BATTER | ValveSO | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | XV-4693G | XV | 4693 | 4693G | L4 BTTR RECIRC TNK PMP CIP VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-46-50-05 | PID | 4 | L4_BATTER | ValveSO | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | XV-4693H | XV | 4693 | 4693H | L4 BTTR RECIRC TNK PMP CIP VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-46-50-05 | PID | 4 | L4_BATTER | ValveSO | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | XV-4693J | XV | 4693 | 4693J | L4 BTTR RECIRC TNK PMP CIP VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-46-50-05 | PID | 4 | L4_BATTER | ValveSO | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | XV-4693K | XV | 4693 | 4693K | L4 BTTR RECIRC TNK PMP CIP VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-46-50-05 | PID | 4 | L4_BATTER | ValveSO | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | XV-4693L | XV | 4693 | 4693L | L4 BTTR RECIRC TNK PMP CIP VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-46-50-05 | PID | 4 | L4_BATTER | ValveSO | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | XV-4695A | XV | 4695 | 4695A | L4 BTTR BLOW OFF BLOWER 1 GLYCOL VLV | AS-I | DI/DO | L04PRC-R2 | Others | [8 empty] | GFP-F-46-50-05 | PID | 4 | L4_BATTER | ValveSO | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | XV-4705A | XV | 4705 | 4705A | L4 A-STAGE FRYER VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-01 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | XV-4705B | XV | 4705 | 4705B | L4 A-STAGE FRYER VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-01 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | XV-4710A | XV | 4710 | 4710A | L4 B-STAGE FRYER VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-01 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4711A | XV | 4711 | 4711A | L4 FRYER OIL AND CRMBS CHUTE VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-01 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | XV-4713A | XV | 4713 | 4713A | L4 FRYER DRIP PAN CIP PMP VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-01 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | XV-4714A | XV | 4714 | 4714A | L4 FRYER DRIP PAN PMP VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-01 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | XV-4715A | XV | 4715 | 4715A | L4 FRYER A-STAGE CONN TNK HOT WTR VLV | AS-I | DI/DO | L04PRC-R2 | Others | [8 empty] | GFP-F-47-50-02 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | XV-4717A | XV | 4717 | 4717A | L4 FRYER A-STAGE ROTARY FLTR 1 VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-02 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | XV-4718A | XV | 4718 | 4718A | L4 FRYER A-STAGE CIRC PMP 1 VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-02 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | XV-4718B | XV | 4718 | 4718B | L4 FRYER A-STAGE CIRC PMP 1 VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-02 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | XV-4719A | XV | 4719 | 4719A | L4 FRYER A-STAGE ROTARY FLTR 2 VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-02 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | XV-4722A | XV | 4722 | 4722A | L4 FRYER A-STAGE DRN PMP DRN VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-02 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | XV-4722B | XV | 4722 | 4722B | L4 FRYER A-STAGE DRN PMP DRN VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-02 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | XV-4722C | XV | 4722 | 4722C | L4 FRYER A-STAGE DRN PMP VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-02 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | XV-4722D | XV | 4722 | 4722D | L4 FRYER A-STAGE DRN PMP VLV | AS-I | DI/DO | L04PRC-R2 | Others | [8 empty] | GFP-F-47-50-02 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | XV-4723A | XV | 4723 | 4723A | L4 DRN TNK CLEAN OIL VLV | AS-I | DI/DO | L04PRC-R2 | Others | [8 empty] | GFP-F-47-50-02 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R2-ASM01
|  | XV-4723C | XV | 4723 | 4723C | L4 DRN TNK DRN VLV | AS-I | DI/DO | L04PRC-R2 | Others | [8 empty] | GFP-F-47-50-02 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R2-ASM01
|  | XV-4725A | XV | 4725 | 4725A | L4 NEW OIL TNK CLEAN OIL VLV | AS-I | DI/DO | L04PRC-R2 | Others | [8 empty] | GFP-F-47-50-02 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | XV-4725B | XV | 4725 | 4725B | L4 NEW OIL TNK VLV | AS-I | DI/DO | L04PRC-R2 | Others | [8 empty] | GFP-F-47-50-02 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | XV-4726B | XV | 4726 | 4726B | L4 FRYER DRN TNK PMP VLV | AS-I | DI/DO | L04PRC-R2 | Others | [8 empty] | GFP-F-47-50-02 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R2-ASM01
|  | XV-4726C | XV | 4726 | 4726C | L4 FRYER DRN TNK PMP VLV | AS-I | DI/DO | L04PRC-R2 | Others | [8 empty] | GFP-F-47-50-02 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R2-ASM01
|  | XV-4728A | XV | 4728 | 4728A | L4 FRYER FAST FILL PMP VLV | AS-I | DI/DO | L04PRC-R2 | Others | [8 empty] | GFP-F-47-50-02 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | XV-4728B | XV | 4728 | 4728B | L4 FRYER FAST FILL PMP VLV | AS-I | DI/DO | L04PRC-R2 | Others | [8 empty] | GFP-F-47-50-02 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | XV-4728C | XV | 4728 | 4728C | L4 FRYER FAST FILL PMP VLV | AS-I | DI/DO | L04PRC-R2 | Others | [8 empty] | GFP-F-47-50-02 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | XV-4728D | XV | 4728 | 4728D | L4 FRYER FAST FILL PMP VLV | AS-I | DI/DO | L04PRC-R2 | Others | [8 empty] | GFP-F-47-50-02 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | XV-4730A | XV | 4730 | 4730A | L4 A-STAGE LAKOS FLTR VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-03 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | XV-4730B | XV | 4730 | 4730B | L4 A-STAGE LAKOS FLTR VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-03 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | XV-4730C | XV | 4730 | 4730C | L4 A-STAGE LAKOS FLTR VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-03 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | XV-4730D | XV | 4730 | 4730D | L4 A-STAGE LAKOS FLTR VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-03 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | XV-4730E | XV | 4730 | 4730E | L4 A-STAGE LAKOS FLTR VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-03 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | XV-4732A | XV | 4732 | 4732A | L4 FRYER A-STAGE HEX VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-03 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | XV-4732B | XV | 4732 | 4732B | L4 FRYER A-STAGE HEX VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-03 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | XV-4732C | XV | 4732 | 4732C | L4 FRYER A-STAGE HEX VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-03 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | XV-4735A | XV | 4735 | 4735A | L4 A-STAGE FRYER OBERLIN FD TNK VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-03 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | XV-4736A | XV | 4736 | 4736A | L4 A-STAGE FRYER OBERLIN FD PMP VLV | AS-I | DI/DO | L04PRC-R2 | Others | [8 empty] | GFP-F-47-50-03 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | XV-4738D | XV | 4738 | 4738D | L4 A-STAGE OBERLIN FLTR VLV | AS-I | DI/DO | L04PRC-R2 | Others | [8 empty] | GFP-F-47-50-06 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | XV-4738E | XV | 4738 | 4738E | L4 A-STAGE OBERLIN FLTR VLV | AS-I | DI/DO | L04PRC-R2 | Others | [8 empty] | GFP-F-47-50-06 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | XV-4739C | XV | 4739 | 4739C | L4 A-STAGE OBERLIN CLEAN OIL PMP VLV | AS-I | DI/DO | L04PRC-R2 | Others | [8 empty] | GFP-F-47-50-06 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | XV-4739D | XV | 4739 | 4739D | L4 A-STAGE OBERLIN CLEAN OIL PMP VLV | AS-I | DI/DO | L04PRC-R2 | Others | [8 empty] | GFP-F-47-50-06 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | XV-4745A | XV | 4745 | 4745A | L4 FRYER B-STAGE CONN TNK VLV | AS-I | DI/DO | L04PRC-R2 | Others | [8 empty] | GFP-F-47-50-04 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4747A | XV | 4747 | 4747A | L4 FRYER B-STAGE ROTARY FLTR 1 VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-04 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4748A | XV | 4748 | 4748A | L4 FRYER B-STAGE CIRC PMP VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-04 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4748B | XV | 4748 | 4748B | L4 FRYER B-STAGE CIRC PMP VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-04 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4749A | XV | 4749 | 4749A | L4 FRYER B-STAGE ROTARY FLTR 2 VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-04 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4753A | XV | 4753 | 4753A | L4 FRYER B-STAGE DRN PMP VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-04 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4753B | XV | 4753 | 4753B | L4 FRYER B-STAGE DRN PMP VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-04 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4753C | XV | 4753 | 4753C | L4 FRYER B-STAGE DRN PMP | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-04 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4757A | XV | 4757 | 4757A | L4 FRYER CRUMB PRESS FD AUGER VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-04 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4759A | XV | 4759 | 4759A | L4 FRYER CRUMB PRESS DRN VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-04 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4759B | XV | 4759 | 4759B | L4 FRYER CRUMB PRESS PMP DRN VLV | AS-I | DI/DO | L04PRC-R2 | Others | [8 empty] | GFP-F-47-50-04 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4765A | XV | 4765 | 4765A | L4 B-STAGE LAKOS FLTR VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-05 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4765B | XV | 4765 | 4765B | L4 B-STAGE LAKOS FLTR VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-05 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4765C | XV | 4765 | 4765C | L4 B-STAGE LAKOS FLTR VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-05 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4765D | XV | 4765 | 4765D | L4 B-STAGE LAKOS FLTR VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-05 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4765E | XV | 4765 | 4765E | L4 B-STAGE LAKOS FLTR VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-05 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4765F | XV | 4765 | 4765F | L4 B-STAGE LAKOS FLTR VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-05 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4765G | XV | 4765 | 4765G | L4 B-STAGE LAKOS FLTR VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-05 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4765H | XV | 4765 | 4765H | L4 B-STAGE LAKOS FLTR VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-05 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4765J | XV | 4765 | 4765J | L4 B-STAGE LAKOS FLTR VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-05 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4767A | XV | 4767 | 4767A | L4 FRYER B-STAGE HEX VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-05 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4767B | XV | 4767 | 4767B | L4 FRYER B-STAGE HEX VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-05 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4767C | XV | 4767 | 4767C | L4 FRYER B-STAGE HEX VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-05 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4770A | XV | 4770 | 4770A | L4 B-STAGE FRYER OBERLIN FD TNK VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-05 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4771A | XV | 4771 | 4771A | L4 B-STAGE FRYER OBERLIN FD PMP VLV | AS-I | DI/DO | L04PRC-R2 | Others | [8 empty] | GFP-F-47-50-05 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4773D | XV | 4773 | 4773D | L4 B-STAGE OBERLIN FLTR VLV | AS-I | DI/DO | L04PRC-R2 | Others | [8 empty] | GFP-F-47-50-07 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4773E | XV | 4773 | 4773E | L4 B-STAGE OBERLIN FLTR VLV | AS-I | DI/DO | L04PRC-R2 | Others | [8 empty] | GFP-F-47-50-07 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4785A | XV | 4785 | 4785A | L4 OIL MISER CNVR VLV | AS-I | DI/DO | L04PRC-R2 | ? | [8 empty] | GFP-F-47-50-09 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4785B | XV | 4785 | 4785B | L4 OIL MISER CNVR VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-09 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4785C | XV | 4785 | 4785C | L4 OIL MISER CNVR VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-09 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4785D | XV | 4785 | 4785D | L4 OIL MISER CNVR VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-09 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4785E | XV | 4785 | 4785E | L4 OIL MISER CNVR VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-09 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4785F | XV | 4785 | 4785F | L4 OIL MISER CNVR VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-09 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4786A | XV | 4786 | 4786A | L4 OIL MISER CYCLONES VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-09 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4786B | XV | 4786 | 4786B | L4 OIL MISER CYCLONES VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-09 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4786C | XV | 4786 | 4786C | L4 OIL MISER CYCLONES VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-09 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4786D | XV | 4786 | 4786D | L4 OIL MISER CYCLONES VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-09 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4786E | XV | 4786 | 4786E | L4 OIL MISER CYCLONES VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-09 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4791A | XV | 4791 | 4791A | L4 OIL MISER CRUMB OIL COLL TNK 1 VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-09 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4792A | XV | 4792 | 4792A | L4 OIL MISER CRUMB OIL COLL TNK 2 VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-09 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4793A | XV | 4793 | 4793A | L4 OIL MISER RETURN PMP VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-09 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4793B | XV | 4793 | 4793B | L4 OIL MISER RETURN PMP VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-09 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4794A | XV | 4794 | 4794A | L4 OIL MISER FAN VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-09 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4794B | XV | 4794 | 4794B | L4 OIL MISER FAN VLV | AS-I | DI/DO | L04PRC-R2 | OEM | [8 empty] | GFP-F-47-50-09 | PID | 4 | L4_FRYER | ValveSO | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | FIT-4670A | FIT | 4670 | 4670A | L4 BTTR HEX FLOW | 4-WIRE | AI | L04PRC-R2-JB01 | RJX |  |  | Tri-Clamp | [5 empty] | GFP-F-46-50-04 | Equipment - Vendor Supplied Items | 4 | L4_BATTER | AIn | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | PIT-4670A | PIT | 4670 | 4670A | L4 BTTR HEX PRESS | 4-WIRE | AI | L04PRC-R2-JB01 | OEM | [8 empty] | GFP-F-46-50-04 | Equipment - Vendor Supplied Items | 4 | L4_BATTER | AIn | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | TIT-4670A | TIT | 4670 | 4670A | L4 BTTR HEX GLYCOL SUPPLY TEMP | 4-WIRE | AI | L04PRC-R2-JB01 | RJX | [8 empty] | GFP-F-46-50-04 | PID | 4 | L4_BATTER | AIn | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | TIT-4670B | TIT | 4670 | 4670B | L4 BTTR HEX TEMP | 4-WIRE | AI | L04PRC-R2-JB01 | RJX | [8 empty] | GFP-F-46-50-04 | PID | 4 | L4_BATTER | AIn | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | LIT-4686A | LIT | 4686 | 4686A | L4 BTTR APP HOLD DWN DRUM LVL | 4-WIRE | AI | L04PRC-R2-JB01 | OEM | [8 empty] | GFP-F-46-50-05 | Equipment - Vendor Supplied Items | 4 | L4_BATTER | AIn | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | TT-4686A | TT | 4686 | 4686A | L4 BTTR APP HOLD DWN DRUM TEMP | 4-WIRE | AI | L04PRC-R2-JB01 | OEM | [8 empty] | GFP-F-46-50-05 | PID | 4 | L4_BATTER | AIn | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | LIT-4692A | LIT | 4692 | 4692A | L4 BTTR RECIRC TNK LVL | 4-WIRE | AI | L04PRC-R2-JB01 | OEM | [8 empty] | GFP-F-46-50-05 | Equipment - Vendor Supplied Items | 4 | L4_BATTER | AIn | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | LIT-4723A | LIT | 4723 | 4723A | L4 DRN TNK LVL | 4-WIRE | AI | L04PRC-R2-JB01 | RJX | [8 empty] | GFP-F-47-50-02 | PID | 4 | L4_FRYER | AIn | LINE 4 FRYER UNIT |  | L04PRC-R2-ASM01
|  | LIT-4665A | LIT | 4665 | 4665A | L4 BTTR HOLDING TNK LVL | 4-WIRE | AI | L04PRC-R2-JB01 | OEM | [8 empty] | GFP-F-46-50-04 | Equipment - Vendor Supplied Items | 4 | L4_BATTER | AIn | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | TT-4665A | TT | 4665 | 4665A | L4 BTTR HOLDING TNK TEMP | 4-WIRE | AI | L04PRC-R2-JB01 | OEM | [8 empty] | GFP-F-46-50-04 | PID | 4 | L4_BATTER | AIn | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | TCV-4670A | TCV | 4670 | 4670A | L4 BTTR HEX TEMP CNTRL VLV | 4-WIRE | AO | L04PRC-R2-JB01 | Others | [8 empty] | GFP-F-46-50-04 | PID | 4 | L4_BATTER | AOut | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | LV-4686A | LV | 4686 | 4686A | L4 BTTR APP HOLD DWN DRUM LVL CNTRL VLV | 4-WIRE | AO | L04PRC-R2-JB01 | OEM | [8 empty] | GFP-F-46-50-05 | PID | 4 | L4_BATTER | AOut | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | ZS-4665A | ZS | 4665 | 4665A | L4 BTTR HOLDING TNK POS | 3-WIRE | DI | L04PRC-R2-JB01 | RJX | [8 empty] | GFP-F-46-50-04 | PID | 4 | L4_BATTER | DIn | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | LSH-4723A | LSH | 4723 | 4723A | L4 DRN TNK LVL HI | 3-WIRE | DI | L04PRC-R2-JB01 | RJX | [8 empty] | GFP-F-47-50-02 | PID | 4 | L4_FRYER | DIn | LINE 4 FRYER UNIT |  | L04PRC-R2-ASM01
|  | SV-4667A | SV | 4667 | 4667A | L4 BTTR HOLDING TNK CHEM PMP AIR VLV | 3-WIRE | RLY | L04PRC-R2-JB01 | Others | [8 empty] | GFP-F-46-50-04 | PID | 4 | L4_BATTER | DOut | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | SV-4693E | SV | 4693 | 4693E | L4 BTTR RECIRC TNK PMP COLD WTRVLV | 3-WIRE | RLY | L04PRC-R2-JB01 | Others | [8 empty] | GFP-F-46-50-05 | PID | 4 | L4_BATTER | DOut | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | HSB-4681A | HSB | 4681 | 4681A | L4 BTTR APP FD SHKRS HND SWTCH BACK | 3-WIRE | DI | L04PRC-R2-JB02 | RJX | [8 empty] | GFP-F-46-50-05 | PID | 4 | L4_BATTER | DIn | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | HSF-4681A | HSF | 4681 | 4681A | L4 BTTR APP FD SHKRS HND SWTCH FWD | 3-WIRE | DI | L04PRC-R2-JB02 | RJX | [8 empty] | GFP-F-46-50-05 | PID | 4 | L4_BATTER | DIn | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | ZSB-4681A | ZSB | 4681 | 4681A | L4 BTTR APP FD SHKRS BACK POS | 3-WIRE | DI | L04PRC-R2-JB02 | OEM | [8 empty] | GFP-F-46-50-05 | PID | 4 | L4_BATTER | DIn | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | ZSF-4681A | ZSF | 4681 | 4681A | L4 BTTR APP FD SHKRS FWD POS | 3-WIRE | DI | L04PRC-R2-JB02 | OEM | [8 empty] | GFP-F-46-50-05 | PID | 4 | L4_BATTER | DIn | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | HSD-4685A | HSD | 4685 | 4685A | L4 BTTR APP HND SWTCH DWN | 3-WIRE | DI | L04PRC-R2-JB02 | RJX | [8 empty] | GFP-F-46-50-05 | PID | 4 | L4_BATTER | DIn | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | HSU-4685A | HSU | 4685 | 4685A | L4 BTTR APP HND SWTCH UP | 3-WIRE | DI | L04PRC-R2-JB02 | RJX | [8 empty] | GFP-F-46-50-05 | PID | 4 | L4_BATTER | DIn | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | SS-4685B | SS | 4685 | 4685B | L4 BTTR APP SPEED SWTCH | 3-WIRE | DI | L04PRC-R2-JB02 | OEM | [8 empty] | GFP-F-46-50-05 | Equipment - Vendor Supplied Items | 4 | L4_BATTER | DIn | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | ZSH-4685A | ZSH | 4685 | 4685A | L4 BTTR APP POS HI | 3-WIRE | DI | L04PRC-R2-JB02 | OEM | [8 empty] | GFP-F-46-50-05 | Equipment - Vendor Supplied Items | 4 | L4_BATTER | DIn | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | ZSL-4685A | ZSL | 4685 | 4685A | L4 BTTR APP POS LIGHT | 3-WIRE | DI | L04PRC-R2-JB02 | OEM | [8 empty] | GFP-F-46-50-05 | Equipment - Vendor Supplied Items | 4 | L4_BATTER | DIn | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | SS-4685A | SS | 4685 | 4685A | L4 BTTR APP SPEED SWTCH | 3-WIRE | DI | L04PRC-R2-JB03 | OEM | [8 empty] | GFP-F-46-50-05 | PID | 4 | L4_BATTER | DIn | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | HSB-4690A | HSB | 4690 | 4690A | L4 A-STAGE FRYER FD CNVR HND SWTCH BACK | 3-WIRE | DI | L04PRC-R2-JB03 | RJX | [8 empty] | GFP-F-46-50-05 | PID | 4 | L4_BATTER | DIn | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | HSF-4690A | HSF | 4690 | 4690A | L4 A-STAGE FRYER FD CNVR HND SWTCH FWD | 3-WIRE | DI | L04PRC-R2-JB03 | RJX | [8 empty] | GFP-F-46-50-05 | PID | 4 | L4_BATTER | DIn | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | ZSB-4690A | ZSB | 4690 | 4690A | L4 A-STAGE FRYER FD CNVR BACK POS | 3-WIRE | DI | L04PRC-R2-JB03 | OEM | [8 empty] | GFP-F-46-50-05 | Equipment - Vendor Supplied Items | 4 | L4_BATTER | DIn | LINE 4 BATTER UNIT |  | L04PRC-R2-ASM01
|  | ZSF-4690A | ZSF | 4690 | 4690A | L4 A-STAGE FRYER FD CNVR FWD POS | 3-WIRE | DI | L04PRC-R2-JB03 | OEM | [8 empty] | GFP-F-46-50-05 | Equipment - Vendor Supplied Items | 4 | L4_BATTER | DIn | LINE 4 BATTER UNIT |  | L04PRC-R3-ASM01
|  | LIT-4710A | LIT | 4710 | 4710A | L4 B-STAGE FRYER LVL | 4-WIRE | AI | L04PRC-R2-JB09 | OEM | [8 empty] | GFP-F-47-50-01 | PID | 4 | L4_FRYER | AIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | TT-4710A | TT | 4710 | 4710A | L4 B-STAGE FRYER TEMP | 4-WIRE | AI | L04PRC-R2-JB09 | OEM | [8 empty] | GFP-F-47-50-01 | PID | 4 | L4_FRYER | AIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | TT-4710B | TT | 4710 | 4710B | L4 B-STAGE FRYER TEMP | 4-WIRE | AI | L04PRC-R2-JB09 | OEM | [8 empty] | GFP-F-47-50-01 | PID | 4 | L4_FRYER | AIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | TT-4710C | TT | 4710 | 4710C | L4 B-STAGE FRYER TEMP | 4-WIRE | AI | L04PRC-R2-JB09 | OEM | [8 empty] | GFP-F-47-50-01 | PID | 4 | L4_FRYER | AIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | TT-4710D | TT | 4710 | 4710D | L4 B-STAGE FRYER TEMP | 4-WIRE | AI | L04PRC-R2-JB09 | OEM | [8 empty] | GFP-F-47-50-01 | PID | 4 | L4_FRYER | AIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | ZSD-4706A | ZSD | 4706 | 4706A | L4 FRYER INFD HOOD BAFFLE POS DWN | 3-WIRE | DI | L04PRC-R3-JB01 | OEM | [8 empty] | GFP-F-47-50-01 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | DIn | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | ZSU-4706B | ZSU | 4706 | 4706B | L4 FRYER INFD HOOD BAFFLE POS UP | 3-WIRE | DI | L04PRC-R3-JB01 | OEM | [8 empty] | GFP-F-47-50-01 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | DIn | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | SV-4705A | SV | 4705 | 4705A | L4 A-STAGE FRYER COLD WTR VLV | 3-WIRE | RLY | L04PRC-R3-JB01 | OEM | [8 empty] | GFP-F-47-50-01 | PID | 4 | L4_FRYER | DOut | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | FIT-4705A | FIT | 4705 | 4705A | L4 A-STAGE FRYER FLOW | 4-WIRE | AI | L04PRC-R3-JB02 | RJX | [8 empty] | GFP-F-47-50-01 | PID | 4 | L4_FRYER | AIn | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | LIT-4705A | LIT | 4705 | 4705A | L4 A-STAGE FRYER LVL | 4-WIRE | AI | L04PRC-R3-JB02 | OEM | [8 empty] | GFP-F-47-50-01 | PID | 4 | L4_FRYER | AIn | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | LIT-4711A | LIT | 4711 | 4711A | L4 FRYER OIL AND CRMBS CHUTE LVL | 4-WIRE | AI | L04PRC-R3-JB02 | OEM | [8 empty] | GFP-F-47-50-01 | PID | 4 | L4_FRYER | AIn | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | PIT-4783A | PIT | 4783 | 4783A | L4 FRYER EXHST FAN PRESS | 4-WIRE | AI | L04PRC-R3-JB02 | RJX | [8 empty] | GFP-F-47-50-08 | PID | 4 | L4_FRYER | AIn | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | TT-4783A | TT | 4783 | 4783A | L4 FRYER EXHST FAN TEMP | 4-WIRE | AI | L04PRC-R3-JB02 | RJX | [8 empty] | GFP-F-47-50-08 | PID | 4 | L4_FRYER | AIn | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | PIT-4783B | PIT | 4783 | 4783B | L4 FRYER EXHST FAN PRESS | 4-WIRE | AI | L04PRC-R3-JB02 | RJX | [8 empty] | GFP-F-47-50-08 | PID | 4 | L4_FRYER | AIn | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | FV-4705A | FV | 4705 | 4705A | L4 A-STAGE FRYER FLOW VLV | 4-WIRE | AO | L04PRC-R3-JB02 | OEM | [8 empty] | GFP-F-47-50-01 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | AOut | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | FV-4705B | FV | 4705 | 4705B | L4 A-STAGE FRYER FLOW VLV | 4-WIRE | AO | L04PRC-R3-JB02 | OEM | [8 empty] | GFP-F-47-50-01 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | AOut | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | FV-4705C | FV | 4705 | 4705C | L4 A-STAGE FRYER FLOW VLV | 4-WIRE | AO | L04PRC-R3-JB02 | OEM | [8 empty] | GFP-F-47-50-01 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | AOut | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | FV-4705D | FV | 4705 | 4705D | L4 A-STAGE FRYER FLOW VLV | 4-WIRE | AO | L04PRC-R3-JB02 | OEM | [8 empty] | GFP-F-47-50-01 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | AOut | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | FV-4705E | FV | 4705 | 4705E | L4 A-STAGE FRYER FLOW VLV | 4-WIRE | AO | L04PRC-R3-JB02 | OEM | [8 empty] | GFP-F-47-50-01 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | AOut | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | FV-4705F | FV | 4705 | 4705F | L4 A-STAGE FRYER FLOW VLV | 4-WIRE | AO | L04PRC-R3-JB02 | OEM | [8 empty] | GFP-F-47-50-01 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | AOut | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | LSH-4705A | LSH | 4705 | 4705A | L4 A-STAGE FRYER LVL HI | 3-WIRE | DI | L04PRC-R3-JB02 | OEM | [8 empty] | GFP-F-47-50-01 | PID | 4 | L4_FRYER | DIn | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | HSD-4706A | HSD | 4706 | 4706A | L4 FRYER INFD HOOD BAFFLE HND SWTCH DWN | 3-WIRE | DI | L04PRC-R3-JB02 | RJX | [8 empty] | GFP-F-47-50-01 | PID | 4 | L4_FRYER | DIn | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | HSU-4706B | HSU | 4706 | 4706B | L4 FRYER INFD HOOD BAFFLE HND SWTCH UP | 3-WIRE | DI | L04PRC-R3-JB02 | RJX | [8 empty] | GFP-F-47-50-01 | PID | 4 | L4_FRYER | DIn | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | LSH-4711A | LSH | 4711 | 4711A | L4 FRYER OIL AND CRMBS CHUTE LVL HI | 3-WIRE | DI | L04PRC-R3-JB02 | OEM | [8 empty] | GFP-F-47-50-01 | PID | 4 | L4_FRYER | DIn | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | LIT-4718A | LIT | 4718 | 4718A | L4 FRYER A-STAGE CIRC PMP 1 LVL | 4-WIRE | AI | L04PRC-R3-JB03 | RJX | [8 empty] | GFP-F-47-50-02 | PID | 4 | L4_FRYER | AIn | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | PIT-4730A | PIT | 4730 | 4730A | L4 A-STAGE LAKOS FLTR PRESS | 4-WIRE | AI | L04PRC-R3-JB03 | OEM | [8 empty] | GFP-F-47-50-03 | PID | 4 | L4_FRYER | AIn | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | PIT-4730B | PIT | 4730 | 4730B | L4 A-STAGE LAKOS FLTR PRESS | 4-WIRE | AI | L04PRC-R3-JB03 | OEM | [8 empty] | GFP-F-47-50-03 | PID | 4 | L4_FRYER | AIn | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | TT-4730A | TT | 4730 | 4730A | L4 A-STAGE LAKOS FLTR TEMP | 4-WIRE | AI | L04PRC-R3-JB03 | OEM | [8 empty] | GFP-F-47-50-03 | PID | 4 | L4_FRYER | AIn | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | FIT-4732A | FIT | 4732 | 4732A | L4 FRYER A-STAGE HEX FLOW | 4-WIRE | AI | L04PRC-R3-JB03 | OEM | [8 empty] | GFP-F-47-50-03 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | AIn | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | LIT-4732A | LIT | 4732 | 4732A | L4 FRYER A-STAGE HEX LVL | 4-WIRE | AI | L04PRC-R3-JB03 | OEM | [8 empty] | GFP-F-47-50-03 | PID | 4 | L4_FRYER | AIn | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | PIT-4732A | PIT | 4732 | 4732A | L4 FRYER A-STAGE HEX PRESS | 4-WIRE | AI | L04PRC-R3-JB03 | RJX | [8 empty] | GFP-F-47-50-03 | PID | 4 | L4_FRYER | AIn | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | PIT-4732B | PIT | 4732 | 4732B | L4 FRYER A-STAGE HEX PRESS | 4-WIRE | AI | L04PRC-R3-JB03 | OEM | [8 empty] | GFP-F-47-50-03 | PID | 4 | L4_FRYER | AIn | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | TT-4732A | TT | 4732 | 4732A | L4 FRYER A-STAGE HEX TEMP | 4-WIRE | AI | L04PRC-R3-JB03 | OEM | [8 empty] | GFP-F-47-50-03 | PID | 4 | L4_FRYER | AIn | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | LIT-4735A | LIT | 4735 | 4735A | L4 A-STAGE FRYER OBERLIN FD TNK LVL | 4-WIRE | AI | L04PRC-R3-JB03 | OEM | [8 empty] | GFP-F-47-50-03 | PID | 4 | L4_FRYER | AIn | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | FV-4732A | FV | 4732 | 4732A | L4 FRYER A-STAGE HEX FLOW VLV | 4-WIRE | AO | L04PRC-R3-JB03 | OEM | [8 empty] | GFP-F-47-50-03 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | AOut | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | LCV-4732A | LCV | 4732 | 4732A | L4 FRYER A-STAGE HEX LVL CNTRL VLV | 4-WIRE | AO | L04PRC-R3-JB03 | OEM | [8 empty] | GFP-F-47-50-03 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | AOut | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | TCV-4732A | TCV | 4732 | 4732A | L4 FRYER A-STAGE HEX TEMP CNTRL VLV | 4-WIRE | AO | L04PRC-R3-JB03 | OEM | [8 empty] | GFP-F-47-50-03 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | AOut | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | ZSS-4717A | ZSS | 4717 | 4717A | L4 FRYER A-STAGE ROTARY FLTR 1 POS | 3-WIRE | DI | L04PRC-R3-JB03 | OEM | [8 empty] | GFP-F-47-50-02 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | DIn | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | FS-4718A | FS | 4718 | 4718A | L4 FRYER A-STAGE CIRC PMP 1 FLOW SWTCH | 3-WIRE | DI | L04PRC-R3-JB03 | OEM | [8 empty] | GFP-F-47-50-02 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | DIn | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | ZSS-4719A | ZSS | 4719 | 4719A | L4 FRYER A-STAGE ROTARY FLTR 2 POS | 3-WIRE | DI | L04PRC-R3-JB03 | OEM | [8 empty] | GFP-F-47-50-02 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | DIn | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | LSH-4735A | LSH | 4735 | 4735A | L4 A-STAGE FRYER OBERLIN FD TNK LVL HI | 3-WIRE | DI | L04PRC-R3-JB03 | OEM | [8 empty] | GFP-F-47-50-03 | PID | 4 | L4_FRYER | DIn | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | SV-4718A | SV | 4718 | 4718A | L4 FRYER A-STAGE CIRC PMP 1 STEAM VLV | 3-WIRE | RLY | L04PRC-R3-JB03 | OEM | [8 empty] | GFP-F-47-50-02 | PID | 4 | L4_FRYER | DOut | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | SV-4720A | SV | 4720 | 4720A | L4 FRYER A-STAGE CIRC PMP 1 VLV | 3-WIRE | RLY | L04PRC-R3-JB03 | OEM | [8 empty] | GFP-F-47-50-02 | PID | 4 | L4_FRYER | DOut | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | TT-4705A | TT | 4705 | 4705A | L4 A-STAGE FRYER TEMP | 4-WIRE | AI | L04PRC-R3-JB04 | OEM | [8 empty] | GFP-F-47-50-01 | PID | 4 | L4_FRYER | AIn | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | TT-4705B | TT | 4705 | 4705B | L4 A-STAGE FRYER TEMP | 4-WIRE | AI | L04PRC-R3-JB04 | OEM | [8 empty] | GFP-F-47-50-01 | PID | 4 | L4_FRYER | AIn | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | TT-4705C | TT | 4705 | 4705C | L4 A-STAGE FRYER TEMP | 4-WIRE | AI | L04PRC-R3-JB04 | OEM | [8 empty] | GFP-F-47-50-01 | PID | 4 | L4_FRYER | AIn | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | LCV-4715A | LCV | 4715 | 4715A | L4 FRYER A-STAGE CONN TNK LVL CNTRL VLV | 4-WIRE | AO | L04PRC-R3-JB04 | OEM | [8 empty] | GFP-F-47-50-02 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | AOut | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | ZS-4715A | ZS | 4715 | 4715A | L4 FRYER A-STAGE CONN TNK POS | 3-WIRE | DI | L04PRC-R3-JB04 | OEM | [8 empty] | GFP-F-47-50-02 | PID | 4 | L4_FRYER | DIn | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | SV-4716A | SV | 4716 | 4716A | L4 FRYER A-STAGE CHEMICAL PUMP AIR VLV | 3-WIRE | RLY | L04PRC-R3-JB04 | Others | [8 empty] | GFP-F-47-50-02 | PID | 4 | L4_FRYER | DOut | LINE 4 FRYER UNIT |  | L04PRC-R3-ASM01
|  | LCV-4745A | LCV | 4745 | 4745A | L4 FRYER B-STAGE CONN TNK LVL CNTRL VLV | 4-WIRE | AO | L04PRC-R4-JB01 | OEM | [8 empty] | GFP-F-47-50-04 | PID | 4 | L4_FRYER | AOut | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | ZS-4745A | ZS | 4745 | 4745A | L4 FRYER B-STAGE CONN TNK POS | 3-WIRE | DI | L04PRC-R4-JB01 | OEM | [8 empty] | GFP-F-47-50-04 | PID | 4 | L4_FRYER | DIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | SS-4755A | SS | 4755 | 4755A | L4 FRYER CRUMB COLL AUGER SPEED | 3-WIRE | DI | L04PRC-R4-JB01 | OEM | [8 empty] | GFP-F-47-50-04 | PID | 4 | L4_FRYER | DIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | SS-4757A | SS | 4757 | 4757A | L4 FRYER CRUMB PRESS FD AUGER SPEED | 3-WIRE | DI | L04PRC-R4-JB01 | OEM | [8 empty] | GFP-F-47-50-04 | PID | 4 | L4_FRYER | DIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | SV-4746A | SV | 4746 | 4746A | L4 FRYER B-STAGE CHEM PMP AIR VLV | 3-WIRE | RLY | L04PRC-R4-JB01 | Others | [8 empty] | GFP-F-47-50-04 | PID | 4 | L4_FRYER | DOut | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | FV-4710A | FV | 4710 | 4710A | L4 B-STAGE FRYER FLOW VLV | 4-WIRE | AO | L04PRC-R4-JB03 | OEM | [8 empty] | GFP-F-47-50-01 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | AOut | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | FV-4710B | FV | 4710 | 4710B | L4 B-STAGE FRYER FLOW VLV | 4-WIRE | AO | L04PRC-R4-JB03 | OEM | [8 empty] | GFP-F-47-50-01 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | AOut | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | FV-4710C | FV | 4710 | 4710C | L4 B-STAGE FRYER FLOW VLV | 4-WIRE | AO | L04PRC-R4-JB03 | OEM | [8 empty] | GFP-F-47-50-01 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | AOut | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | FV-4710D | FV | 4710 | 4710D | L4 B-STAGE FRYER FLOW VLV | 4-WIRE | AO | L04PRC-R4-JB03 | OEM | [8 empty] | GFP-F-47-50-01 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | AOut | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | FV-4710E | FV | 4710 | 4710E | L4 B-STAGE FRYER FLOW VLV | 4-WIRE | AO | L04PRC-R4-JB03 | OEM | [8 empty] | GFP-F-47-50-01 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | AOut | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | FV-4710F | FV | 4710 | 4710F | L4 B-STAGE FRYER FLOW VLV | 4-WIRE | AO | L04PRC-R4-JB03 | OEM | [8 empty] | GFP-F-47-50-01 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | AOut | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | FV-4710G | FV | 4710 | 4710G | L4 B-STAGE FRYER FLOW VLV | 4-WIRE | AO | L04PRC-R4-JB03 | OEM | [8 empty] | GFP-F-47-50-01 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | AOut | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | FV-4710H | FV | 4710 | 4710H | L4 B-STAGE FRYER FLOW VLV | 4-WIRE | AO | L04PRC-R4-JB03 | OEM | [8 empty] | GFP-F-47-50-01 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | AOut | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | LSH-4710A | LSH | 4710 | 4710A | L4 B-STAGE FRYER LVL HI | 3-WIRE | DI | L04PRC-R4-JB03 | OEM | [8 empty] | GFP-F-47-50-01 | PID | 4 | L4_FRYER | DIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | HSD-4707A | HSD | 4707 | 4707A | L4 FRYER HOOD JACK HND SWTCH DWN | 3-WIRE | DI | L04PRC-R4-JB04 | RJX | [8 empty] | GFP-F-47-50-01 | PID | 4 | L4_FRYER | DIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | HSU-4707B | HSU | 4707 | 4707B | L4 FRYER HOOD JACK HND SWTCH UP | 3-WIRE | DI | L04PRC-R4-JB04 | RJX | [8 empty] | GFP-F-47-50-01 | PID | 4 | L4_FRYER | DIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | SS-4707A | SS | 4707 | 4707A | L4 FRYER HOOD JACK SPEED | 3-WIRE | DI | L04PRC-R4-JB04 | OEM | [8 empty] | GFP-F-47-50-01 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | DIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | SS-4707B | SS | 4707 | 4707B | L4 FRYER HOOD JACK SPEED | 3-WIRE | DI | L04PRC-R4-JB04 | OEM | [8 empty] | GFP-F-47-50-01 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | DIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | ZSD-4707A | ZSD | 4707 | 4707A | L4 FRYER HOOD JACK POS DWN | 3-WIRE | DI | L04PRC-R4-JB04 | OEM | [8 empty] | GFP-F-47-50-01 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | DIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | ZSU-4707B | ZSU | 4707 | 4707B | L4 FRYER HOOD JACK POS UP | 3-WIRE | DI | L04PRC-R4-JB04 | OEM | [8 empty] | GFP-F-47-50-01 | PID | 4 | L4_FRYER | DIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | LIT-4748A | LIT | 4748 | 4748A | L4 FRYER B-STAGE CIRC PMP LVL | 4-WIRE | AI | L04PRC-R4-JB05 | RJX | [8 empty] | GFP-F-47-50-04 | PID | 4 | L4_FRYER | AIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | PIT-4765A | PIT | 4765 | 4765A | L4 B-STAGE LAKOS FLTR PRESS | 4-WIRE | AI | L04PRC-R4-JB05 | OEM | [8 empty] | GFP-F-47-50-05 | PID | 4 | L4_FRYER | AIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | PIT-4765B | PIT | 4765 | 4765B | L4 B-STAGE LAKOS FLTR PRESS | 4-WIRE | AI | L04PRC-R4-JB05 | OEM | [8 empty] | GFP-F-47-50-05 | PID | 4 | L4_FRYER | AIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | TT-4765A | TT | 4765 | 4765A | L4 B-STAGE LAKOS FLTR TEMP | 4-WIRE | AI | L04PRC-R4-JB05 | OEM | [8 empty] | GFP-F-47-50-05 | PID | 4 | L4_FRYER | AIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | FIT-4767A | FIT | 4767 | 4767A | L4 FRYER B-STAGE HEX FLOW | 4-WIRE | AI | L04PRC-R4-JB05 | OEM | [8 empty] | GFP-F-47-50-05 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | AIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | LIT-4767A | LIT | 4767 | 4767A | L4 FRYER B-STAGE HEX LVL | 4-WIRE | AI | L04PRC-R4-JB05 | OEM | [8 empty] | GFP-F-47-50-05 | PID | 4 | L4_FRYER | AIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | PIT-4767A | PIT | 4767 | 4767A | L4 FRYER B-STAGE HEX PRESS | 4-WIRE | AI | L04PRC-R4-JB05 | RJX | [8 empty] | GFP-F-47-50-05 | PID | 4 | L4_FRYER | AIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | PIT-4767B | PIT | 4767 | 4767B | L4 FRYER B-STAGE HEX PRESS | 4-WIRE | AI | L04PRC-R4-JB05 | OEM | [8 empty] | GFP-F-47-50-05 | PID | 4 | L4_FRYER | AIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | TT-4767A | TT | 4767 | 4767A | L4 FRYER B-STAGE HEX TEMP | 4-WIRE | AI | L04PRC-R4-JB05 | OEM | [8 empty] | GFP-F-47-50-05 | PID | 4 | L4_FRYER | AIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | LIT-4770A | LIT | 4770 | 4770A | L4 B-STAGE FRYER OBERLIN FD TNK LVL | 4-WIRE | AI | L04PRC-R4-JB05 | OEM | [8 empty] | GFP-F-47-50-05 | PID | 4 | L4_FRYER | AIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | FV-4767A | FV | 4767 | 4767A | L4 FRYER B-STAGE HEX FLOW VLV | 4-WIRE | AO | L04PRC-R4-JB05 | OEM | [8 empty] | GFP-F-47-50-05 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | AOut | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | TCV-4767A | TCV | 4767 | 4767A | L4 FRYER B-STAGE HEX TEMP CNTRL VLV | 4-WIRE | AO | L04PRC-R4-JB05 | OEM | [8 empty] | GFP-F-47-50-05 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | AOut | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | ZSS-4747A | ZSS | 4747 | 4747A | L4 FRYER B-STAGE ROTARY FLTR 1 POS | 3-WIRE | DI | L04PRC-R4-JB05 | OEM | [8 empty] | GFP-F-47-50-04 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | DIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | FS-4748A | FS | 4748 | 4748A | L4 FRYER B-STAGE CIRC PMP FLOW SWTCH | 3-WIRE | DI | L04PRC-R4-JB05 | OEM | [8 empty] | GFP-F-47-50-04 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | DIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | ZSS-4749A | ZSS | 4749 | 4749A | L4 FRYER B-STAGE ROTARY FLTR 2 POS | 3-WIRE | DI | L04PRC-R4-JB05 | OEM | [8 empty] | GFP-F-47-50-04 | Equipment - Vendor Supplied Items | 4 | L4_FRYER | DIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | LSH-4770A | LSH | 4770 | 4770A | L4 B-STAGE FRYER OBERLIN FD TNK LVL HI | 3-WIRE | DI | L04PRC-R4-JB05 | OEM | [8 empty] | GFP-F-47-50-05 | PID | 4 | L4_FRYER | DIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | SV-4748A | SV | 4748 | 4748A | L4 FRYER B-STAGE CIRC PMP 1 STEAM VLV | 3-WIRE | RLY | L04PRC-R4-JB05 | OEM | [8 empty] | GFP-F-47-50-02 | PID | 4 | L4_FRYER | DOut | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | SV-4750A | SV | 4750 | 4750A | L4 FRYER B-STAGE CIRC PMP VLV | 3-WIRE | RLY | L04PRC-R4-JB05 | OEM | [8 empty] | GFP-F-47-50-04 | PID | 4 | L4_FRYER | DOut | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | LIT-4791A | LIT | 4791 | 4791A | L4 OIL MISER CRUMB OIL COLL TNK 1 LVL | 4-WIRE | AI | L04PRC-R4-JB06 | RJX | [8 empty] | GFP-F-47-50-09 | PID | 4 | L4_FRYER | AIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | LIT-4792A | LIT | 4792 | 4792A | L4 OIL MISER CRUMB OIL COLL TNK 2 LVL | 4-WIRE | AI | L04PRC-R4-JB06 | ? | [8 empty] | GFP-F-47-50-09 | PID | 4 | L4_FRYER | AIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | ZSS-4785A | ZSS | 4785 | 4785A | L4 OIL MISER CNVR DOOR SFTY SWTCH | 3-WIRE | DI | L04PRC-R4-JB06 | OEM | [8 empty] | GFP-F-47-50-09 | PID | 4 | L4_FRYER | DIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | ZSS-4785B | ZSS | 4785 | 4785B | L4 OIL MISER CNVR DOOR SFTY SWTCH | 3-WIRE | DI | L04PRC-R4-JB06 | OEM | [8 empty] | GFP-F-47-50-09 | PID | 4 | L4_FRYER | DIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | ZSS-4785C | ZSS | 4785 | 4785C | L4 OIL MISER CNVR DOOR SFTY SWTCH | 3-WIRE | DI | L04PRC-R4-JB06 | OEM | [8 empty] | GFP-F-47-50-09 | PID | 4 | L4_FRYER | DIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | ZSS-4785D | ZSS | 4785 | 4785D | L4 OIL MISER CNVR DOOR SFTY SWTCH | 3-WIRE | DI | L04PRC-R4-JB06 | OEM | [8 empty] | GFP-F-47-50-09 | PID | 4 | L4_FRYER | DIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | ZSS-4785E | ZSS | 4785 | 4785E | L4 OIL MISER CNVR DOOR SFTY SWTCH | 3-WIRE | DI | L04PRC-R4-JB06 | OEM | [8 empty] | GFP-F-47-50-09 | PID | 4 | L4_FRYER | DIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | ZSS-4785F | ZSS | 4785 | 4785F | L4 OIL MISER CNVR DOOR SFTY SWTCH | 3-WIRE | DI | L04PRC-R4-JB06 | OEM | [8 empty] | GFP-F-47-50-09 | PID | 4 | L4_FRYER | DIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | ZSS-4785G | ZSS | 4785 | 4785G | L4 OIL MISER CNVR DOOR SFTY SWTCH | 3-WIRE | DI | L04PRC-R4-JB06 | OEM | [8 empty] | GFP-F-47-50-09 | PID | 4 | L4_FRYER | DIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | ZSS-4785H | ZSS | 4785 | 4785H | L4 OIL MISER CNVR DOOR SFTY SWTCH | 3-WIRE | DI | L04PRC-R4-JB06 | OEM | [8 empty] | GFP-F-47-50-09 | PID | 4 | L4_FRYER | DIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | ZSS-4785J | ZSS | 4785 | 4785J | L4 OIL MISER CNVR DOOR SFTY SWTCH | 3-WIRE | DI | L04PRC-R4-JB06 | OEM | [8 empty] | GFP-F-47-50-09 | PID | 4 | L4_FRYER | DIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | ZSS-4785K | ZSS | 4785 | 4785K | L4 OIL MISER CNVR DOOR SFTY SWTCH | 3-WIRE | DI | L04PRC-R4-JB06 | OEM | [8 empty] | GFP-F-47-50-09 | PID | 4 | L4_FRYER | DIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | ZSS-4785L | ZSS | 4785 | 4785L | L4 OIL MISER CNVR DOOR SFTY SWTCH | 3-WIRE | DI | L04PRC-R4-JB06 | OEM | [8 empty] | GFP-F-47-50-09 | PID | 4 | L4_FRYER | DIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | ZSS-4785M | ZSS | 4785 | 4785M | L4 OIL MISER CNVR DOOR SFTY SWTCH | 3-WIRE | DI | L04PRC-R4-JB06 | OEM | [8 empty] | GFP-F-47-50-09 | PID | 4 | L4_FRYER | DIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | ZSS-4785N | ZSS | 4785 | 4785N | L4 OIL MISER CNVR DOOR SFTY SWTCH | 3-WIRE | DI | L04PRC-R4-JB06 | OEM | [8 empty] | GFP-F-47-50-09 | PID | 4 | L4_FRYER | DIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | LSH-4791A | LSH | 4791 | 4791A | L4 OIL MISER CRUMB OIL COLL TNK 1 LVL HI | 3-WIRE | DI | L04PRC-R4-JB06 | OEM | [8 empty] | GFP-F-47-50-09 | PID | 4 | L4_FRYER | DIn | LINE 4 FRYER UNIT |  | L04PRC-R4-ASM01
|  | XV-4610A | XV | 4610 | 4610A | BTTR WTR COOLING HEX RECIRC VLV | AS-I | DI/DO | L04PRC-R5 | Others | [8 empty] | GFP-F-46-50-01 | PID | 4 | L4_BATTER | D4SDTag | LINE 4 BATTER UNIT |  | L04PRC-R5-ASM01
|  | XV-4616A | XV | 4616 | 4616A | L4 BEER STORAGE TNK CIP VLV | AS-I | DI/DO | L04PRC-R5 | Others | [8 empty] | GFP-F-46-50-01 | PID | 4 | L4_BATTER | ValveSO | LINE 4 BATTER UNIT |  | L04PRC-R5-ASM01
|  | XV-4616B | XV | 4616 | 4616B | L4 BEER STORAGE TNK HOT WTR VLV | AS-I | DI/DO | L04PRC-R5 | Others | [8 empty] | GFP-F-46-50-01 | PID | 4 | L4_BATTER | ValveSO | LINE 4 BATTER UNIT |  | L04PRC-R5-ASM01
|  | XV-4616D | XV | 4616 | 4616D | L4 BEER STORAGE TNK DRN VLV | AS-I | DI/DO | L04PRC-R5 | Others | [8 empty] | GFP-F-46-50-01 | PID | 4 | L4_BATTER | ValveSO | LINE 4 BATTER UNIT |  | L04PRC-R5-ASM01
|  | XV-4619A | XV | 4619 | 4619A | BEER COOLING HEX RECIRC VLV | AS-I | DI/DO | L04PRC-R5 | Others | [8 empty] | GFP-F-46-50-01 | PID | 4 | L4_BATTER | D4SDTag | LINE 4 BATTER UNIT |  | L04PRC-R5-ASM01
|  | XV-4619B | XV | 4619 | 4619B | BEER COOLING HEX DRN VLV | AS-I | DI/DO | L04PRC-R5 | Others | [8 empty] | GFP-F-46-50-01 | PID | 4 | L4_BATTER | ValveSO | LINE 4 BATTER UNIT |  | L04PRC-R5-ASM01
|  | XV-4659A | XV | 4659 | 4659A | L4 BTTR ABORT CHUTE DIVERT GATE | AS-I | DI/DO | L04PRC-R5 | OEM | [8 empty] | GFP-F-46-50-03 | PID | 4 | L4_BATTER | ValveSO | LINE 4 BATTER UNIT |  | L04PRC-R5-ASM01
|  | XV-4660C | XV | 4660 | 4660C | L4 BTTR MIX TNK HOT WTR VLV | AS-I | DI/DO | L04PRC-R5 | Others | [8 empty] | GFP-F-46-50-03 | PID | 4 | L4_BATTER | ValveSO | LINE 4 BATTER UNIT |  | L04PRC-R5-ASM01
|  | XV-4660D | XV | 4660 | 4660D | L4 BTTR MIX TNK DRN VLV | AS-I | DI/DO | L04PRC-R5 | OEM | [8 empty] | GFP-F-46-50-03 | Equipment - Vendor Supplied Items | 4 | L4_BATTER | ValveSO | LINE 4 BATTER UNIT |  | L04PRC-R5-ASM01
|  | XV-4660E | XV | 4660 | 4660E | L4 BTTR MIX TNK WTR VLV | AS-I | DI/DO | L04PRC-R5 | Others | [8 empty] | GFP-F-46-50-03 | PID | 4 | L4_BATTER | D4SDTag | LINE 4 BATTER UNIT |  | L04PRC-R5-ASM01
|  | XV-4660F | XV | 4660 | 4660F | L4 BTTR MIX TNK WTR VLV | AS-I | DI/DO | L04PRC-R5 | Others | [8 empty] | GFP-F-46-50-03 | PID | 4 | L4_BATTER | ValveSO | LINE 4 BATTER UNIT |  | L04PRC-R5-ASM01
|  | XV-4660G | XV | 4660 | 4660G | L4 BTTR MIX TNK GLYCOL VLV | AS-I | DI/DO | L04PRC-R5 | Others | [8 empty] | GFP-F-46-50-03 | PID | 4 | L4_BATTER | ValveSO | LINE 4 BATTER UNIT |  | L04PRC-R5-ASM01
|  | XV-4662A | XV | 4662 | 4662A | L4 MIXED BTTR TRANSFER PMP AIR VLV | AS-I | DI/DO | L04PRC-R5 | Others | [8 empty] | GFP-F-46-50-03 | PID | 4 | L4_BATTER | ValveSO | LINE 4 BATTER UNIT |  | L04PRC-R5-ASM01
|  | TT-4605B | TT | 4605 | 4605B | BTTR WTR FLTR A TEMP | 4-WIRE | AI | L04PRC-R5-JB01 | RJX | [8 empty] | GFP-F-46-50-01 | PID | 4 | L4_BATTER | AIn | LINE 4 BATTER UNIT |  | L04PRC-R5-ASM01
|  | PIT-4610A | PIT | 4610 | 4610A | BTTR WTR COOLING HEX PRESS | 4-WIRE | AI | L04PRC-R5-JB01 | RJX | [8 empty] | GFP-F-46-50-01 | PID | 4 | L4_BATTER | AIn | LINE 4 BATTER UNIT |  | L04PRC-R5-ASM01
|  | PIT-4610B | PIT | 4610 | 4610B | BTTR WTR COOLING HEX PRESS | 4-WIRE | AI | L04PRC-R5-JB01 | RJX | [8 empty] | GFP-F-46-50-01 | PID | 4 | L4_BATTER | AIn | LINE 4 BATTER UNIT |  | L04PRC-R5-ASM01
|  | TT-4610B | TT | 4610 | 4610B | BTTR WTR COOLING HEX TEMP | 4-WIRE | AI | L04PRC-R5-JB01 | RJX | [8 empty] | GFP-F-46-50-01 | PID | 4 | L4_BATTER | AIn | LINE 4 BATTER UNIT |  | L04PRC-R5-ASM01
|  | TT-4610C | TT | 4610 | 4610C | BTTR WTR COOLING HEX TEMP | 4-WIRE | AI | L04PRC-R5-JB01 | RJX | [8 empty] | GFP-F-46-50-01 | PID | 4 | L4_BATTER | AIn | LINE 4 BATTER UNIT |  | L04PRC-R5-ASM01
|  | FS-4611A | FS | 4611 | 4611A | BTTR WTR RECIRC PMP FLOW | 3-WIRE | DI | L04PRC-R5-JB01 | RJX | [8 empty] | GFP-F-46-50-01 | PID | 4 | L4_BATTER | DIn | LINE 4 BATTER UNIT |  | L04PRC-R5-ASM01
|  | LIT-4616A | LIT | 4616 | 4616A | L4 BEER STORAGE TNK LVL | 4-WIRE | AI | L04PRC-R5-JB02 | RJX | [8 empty] | GFP-F-46-50-01 | PID | 4 | L4_BATTER | AIn | LINE 4 BATTER UNIT |  | L04PRC-R5-ASM01
|  | TT-4616B | TT | 4616 | 4616B | L4 BEER STORAGE TNK TEMP | 4-WIRE | AI | L04PRC-R5-JB02 | RJX | [8 empty] | GFP-F-46-50-01 | PID | 4 | L4_BATTER | AIn | LINE 4 BATTER UNIT |  | L04PRC-R5-ASM01
|  | TT-4619A | TT | 4619 | 4619A | BEER COOLING HEX TEMP | 4-WIRE | AI | L04PRC-R5-JB02 | RJX | [8 empty] | GFP-F-46-50-01 | PID | 4 | L4_BATTER | AIn | LINE 4 BATTER UNIT |  | L04PRC-R5-ASM01
|  | ZS-4615A | ZS | 4615 | 4615A | BEER UNLOADING PMP POS | 3-WIRE | DI | L04PRC-R5-JB02 | RJX | [8 empty] | GFP-F-46-50-01 | PID | 4 | L4_BATTER | DIn | LINE 4 BATTER UNIT |  | L04PRC-R5-ASM01
|  | ZS-4615B | ZS | 4615 | 4615B | BEER UNLOADING PMP POS | 3-WIRE | DI | L04PRC-R5-JB02 | RJX | [8 empty] | GFP-F-46-50-01 | PID | 4 | L4_BATTER | DIn | LINE 4 BATTER UNIT |  | L04PRC-R5-ASM01
|  | ZSS-4628A | ZSS | 4628 | 4628A | L4 BTTR BAG DUST COLLECTOR A SFTY SWTCH | 3-WIRE | DI | L04PRC-R5-JB02 | OEM | [8 empty] | GFP-F-46-50-02 | PID | 4 | L4_BATTER | DIn | LINE 4 BATTER UNIT |  | L04PRC-R5-ASM01
|  | LSH-4629A | LSH | 4629 | 4629A | L4 BTTR UNLOAD HPPR A LVL HI | 3-WIRE | DI | L04PRC-R5-JB02 | OEM | [8 empty] | GFP-F-46-50-02 | Equipment - Vendor Supplied Items | 4 | L4_BATTER | DIn | LINE 4 BATTER UNIT |  | L04PRC-R5-ASM01
|  | LSL-4629B | LSL | 4629 | 4629B | L4 BTTR UNLOAD HPPR A LVL LIGHT | 3-WIRE | DI | L04PRC-R5-JB02 | OEM | [8 empty] | GFP-F-46-50-02 | Equipment - Vendor Supplied Items | 4 | L4_BATTER | DIn | LINE 4 BATTER UNIT |  | L04PRC-R5-ASM01
|  | SV-4617A | SV | 4617 | 4617A | L4 BEER TNK CAUSTIC PMP AIR VLV | 3-WIRE | RLY | L04PRC-R5-JB02 | Others | [8 empty] | GFP-F-46-50-01 | PID | 4 | L4_BATTER | DOut | LINE 4 BATTER UNIT |  | L04PRC-R5-ASM01
|  | SV-4628A | SV | 4628 | 4628A | L4 BTTR BAG DUST COLLECTOR A VLV | 3-WIRE | RLY | L04PRC-R5-JB02 | OEM | [8 empty] | GFP-F-46-50-02 | Equipment - Vendor Supplied Items | 4 | L4_BATTER | DOut | LINE 4 BATTER UNIT |  | L04PRC-R5-ASM01
|  | SV-4632A | SV | 4632 | 4632A | L4 BTTR BAG UNLOADER AUGER A AIR VLV | 3-WIRE | RLY | L04PRC-R5-JB02 | OEM | [8 empty] | GFP-F-46-50-02 | PID | 4 | L4_BATTER | DOut | LINE 4 BATTER UNIT |  | L04PRC-R5-ASM01
|  | FIT-4660A | FIT | 4660 | 4660A | L4 BTTR MIX TNK FLOW | 4-WIRE | AI | L04PRC-R5-JB03 | RJX |  |  | Tri-Clamp | [5 empty] | GFP-F-46-50-03 | PID | 4 | L4_BATTER | AIn | LINE 4 BATTER UNIT |  | L04PRC-R5-ASM01
|  | TT-4660A | TT | 4660 | 4660A | L4 BTTR MIX TNK TEMP | 4-WIRE | AI | L04PRC-R5-JB03 | ? | [8 empty] | GFP-F-46-50-03 | PID | 4 | L4_BATTER | AIn | LINE 4 BATTER UNIT |  | L04PRC-R5-ASM01
|  | WIT-4655D | WIT | 4655 | 4655D | L4 BTTR WEIGH HPPR WEIGHT | ETHERNET | ETHERNET | L04PRC-R5-JB03 | RJX | [8 empty] | GFP-F-46-50-03 | PID | 4 | L4_BATTER | AIn | LINE 4 BATTER UNIT |  | L04PRC-R5-ASM01
|  | WIT-4660D | WIT | 4660 | 4660D | L4 BTTR MIX TNK WEIGHT | ETHERNET | ETHERNET | L04PRC-R5-JB03 | RJX | [8 empty] | GFP-F-46-50-03 | PID | 4 | L4_BATTER | AIn | LINE 4 BATTER UNIT |  | L04PRC-R5-ASM01
|  | SV-4655A | SV | 4655 | 4655A | L4 BTTR WEIGH HPPR AIR VLV | 3-WIRE | RLY | L04PRC-R5-JB03 | OEM | [8 empty] | GFP-F-46-50-03 | Equipment - Vendor Supplied Items | 4 | L4_BATTER | DOut | LINE 4 BATTER UNIT |  | L04PRC-R5-ASM01
|  | SV-4656B | SV | 4655 | 4656B | L4 BTTR WEIGH HPPR ROTARY VLV AIR VLV | 3-WIRE | RLY | L04PRC-R5-JB03 | OEM | [8 empty] | GFP-F-46-50-03 | Equipment - Vendor Supplied Items | 4 | L4_BATTER | DOut | LINE 4 BATTER UNIT |  | L04PRC-R5-ASM01
|  | SV-4663A | SV | 4663 | 4663A | L4 BTTR MIX CHEM PMP 1 AIR VLV | 3-WIRE | RLY | L04PRC-R5-JB03 | Others | [8 empty] | GFP-F-46-50-03 | PID | 4 | L4_BATTER | DOut | LINE 4 BATTER UNIT |  | L04PRC-R5-ASM01
|  | SV-4664A | SV | 4664 | 4664A | L4 BTTR MIX CHEM PMP 2 AIR VLV | 3-WIRE | RLY | L04PRC-R5-JB03 | Others | [8 empty] | GFP-F-46-50-03 | PID | 4 | L4_BATTER | DOut | LINE 4 BATTER UNIT |  | L04PRC-R5-ASM01
|  | LIT-4910C | LIT | 4910 | 4910C | L4 TOTE-OFF SHAKER 1 TOTE 1 LVL | 4-WIRE | AI | L04PRC-R6-JB01 | RJX | [8 empty] | GFP-F-49-50-01 | PID | 4 | L4_TOTE | AIn | LINE 4 TOTE OFF UNIT |  | L04PRC-R6-ASM01
|  | LIT-4910E | LIT | 4910 | 4910E | L4 TOTE-OFF SHAKER 1 TOTE 2 LVL | 4-WIRE | AI | L04PRC-R6-JB01 | RJX | [8 empty] | GFP-F-49-50-01 | PID | 4 | L4_TOTE | AIn | LINE 4 TOTE OFF UNIT |  | L04PRC-R6-ASM01
|  | ZS-4910D | ZS | 4910 | 4910D | L4 TOTE-OFF SHAKER 1 TOTE 1 POS | 3-WIRE | DI | L04PRC-R6-JB01 | RJX | [8 empty] | GFP-F-49-50-01 | PID | 4 | L4_TOTE | DIn | LINE 4 TOTE OFF UNIT |  | L04PRC-R6-ASM01
|  | ZS-4910F | ZS | 4910 | 4910F | L4 TOTE-OFF SHAKER 1 TOTE 2 POS | 3-WIRE | DI | L04PRC-R6-JB01 | RJX | [8 empty] | GFP-F-49-50-01 | PID | 4 | L4_TOTE | DIn | LINE 4 TOTE OFF UNIT |  | L04PRC-R6-ASM01
|  | XV-4910A | XV | 4910 | 4910A | L4 TOTE-OFF SHAKER 1 DIVERT GATE 1 | 3-WIRE | DO | L04PRC-R6-JB01 | OEM | [8 empty] | GFP-F-49-50-01 | PID | 4 | L4_TOTE | ValveSO | LINE 4 TOTE OFF UNIT |  | L04PRC-R6-ASM01
|  | XV-4910B | XV | 4910 | 4910B | L4 TOTE-OFF SHAKER 1 DIVERT GATE 2 | 3-WIRE | DO | L04PRC-R6-JB01 | OEM | [8 empty] | GFP-F-49-50-01 | PID | 4 | L4_TOTE | ValveSO | LINE 4 TOTE OFF UNIT |  | L04PRC-R6-ASM01
|  | LIT-4912A | LIT | 4912 | 4912A | L4 TOTE-OFF SHAKER 2 TOTE 1 LVL | 4-WIRE | AI | L04PRC-R6-JB02 | RJX | [8 empty] | GFP-F-49-50-01 | PID | 4 | L4_TOTE | AIn | LINE 4 TOTE OFF UNIT |  | L04PRC-R6-ASM01
|  | LIT-4912C | LIT | 4912 | 4912C | L4 TOTE-OFF SHAKER 2 TOTE 2 LVL | 4-WIRE | AI | L04PRC-R6-JB02 | RJX | [8 empty] | GFP-F-49-50-01 | PID | 4 | L4_TOTE | AIn | LINE 4 TOTE OFF UNIT |  | L04PRC-R6-ASM01
|  | ZS-4912B | ZS | 4912 | 4912B | L4 TOTE-OFF SHAKER 2 TOTE 1 POS | 3-WIRE | DI | L04PRC-R6-JB02 | RJX | [8 empty] | GFP-F-49-50-01 | PID | 4 | L4_TOTE | DIn | LINE 4 TOTE OFF UNIT |  | L04PRC-R6-ASM01
|  | ZS-4912D | ZS | 4912 | 4912D | L4 TOTE-OFF SHAKER 2 TOTE 2 POS | 3-WIRE | DI | L04PRC-R6-JB02 | RJX | [8 empty] | GFP-F-49-50-01 | PID | 4 | L4_TOTE | DIn | LINE 4 TOTE OFF UNIT |  | L04PRC-R6-ASM01
|  | XV-4912A | XV | 4912 | 4912A | L4 TOTE-OFF SHAKER 2 DIVERT GATE | 3-WIRE | DO | L04PRC-R6-JB02 | OEM | [8 empty] | GFP-F-49-50-01 | PID | 4 | L4_TOTE | ValveSO | LINE 4 TOTE OFF UNIT |  | L04PRC-R6-ASM01
|  | WIT-4915A | WIT | 4915 | 4915A | L4 FROZEN GRADING FD WEIGH BELT WEIGHT | ETHERNET | ETHERNET | L04PRC-R6-JB03 | RJX | [8 empty] | GFP-F-49-50-01 | PID | 4 | L4_TOTE | AIn | LINE 4 TOTE OFF UNIT |  | L04PRC-R6-ASM01
|  | LIT-4860A | LIT | 4860 | 4860A | L4 FREEZE TUNNEL SUMP LEVEL | 4-WIRE | AI | L04PRC-R6-JB04 | RJX | [8 empty] | GFP-F-48-50-03 | PID | 4 | L4_SUMP | AIn | LINE 4 SUMP UNIT |  | L04PRC-R6-ASM01
|  | LIT-4738A | LIT | 4738 | 4738A | L4 A-STAGE OBERLIN FLTR LVL | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-47-50-06 | Equipment - Vendor Supplied Items | 4 | OEM
|  | LSH-4738A | LSH | 4738 | 4738A | L4 A-STAGE OBERLIN FLTR LVL HI | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-47-50-06 | PID | 4 | OEM
|  | TT-4738A | TT | 4738 | 4738A | L4 A-STAGE OBERLIN FLTR TEMP | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-47-50-06 | Equipment - Vendor Supplied Items | 4 | OEM
|  | XV-4739A | XV | 4739 | 4739A | L4 A-STAGE OBERLIN CLEAN OIL PMP VLV | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-47-50-06 | PID | 4 | OEM
|  | LSH-4773A | LSH | 4773 | 4773A | L4 B-STAGE OBERLIN FLTR LVL HI | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-47-50-07 | Equipment - Vendor Supplied Items | 4 | OEM
|  | TT-4773A | TT | 4773 | 4773A | L4 B-STAGE OBERLIN FLTR TEMP | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-47-50-07 | Equipment - Vendor Supplied Items | 4 | OEM
|  | XV-4774A | XV | 4774 | 4774A | L4 B-STAGE OBERLIN CLEAN OIL PMP VLV | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-47-50-07 | PID | 4 | OEM
|  | AIT-4805A | AIT | 4805 | 4805A | L4 PRECOOL AMONIA | OEM | OEM | OEM | RJX | [8 empty] | GFP-F-48-50-01 | PID | 4 | OEM
|  | ES-4805A | ES | 4805 | 4805A | L4 REFRIGERATED PRECOOL E-STOP | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-48-50-01 | Equipment - Vendor Supplied Items | 4 | OEM
|  | ES-4805B | ES | 4805 | 4805B | L4 REFRIGERATED PRECOOL VOLTAGE | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-48-50-01 | Equipment - Vendor Supplied Items | 4 | OEM
|  | ES-4805C | ES | 4805 | 4805C | L4 REFRIGERATED PRECOOL E-STOP | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-48-50-01 | Equipment - Vendor Supplied Items | 4 | OEM
|  | HS-4805A | HS | 4805 | 4805A | L4 REFRIGERATED PRECOOL HND SWTCH | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-48-50-01 | PID | 4 | OEM
|  | HS-4805B | HS | 4805 | 4805B | L4 REFRIGERATED PRECOOL HND SWTCH | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-48-50-01 | PID | 4 | OEM
|  | HS-4805C | HS | 4805 | 4805C | L4 REFRIGERATED PRECOOL HND SWTCH | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-48-50-01 | PID | 4 | OEM
|  | LIT-4805A | LIT | 4805 | 4805A | L4 REFRIGERATED PRECOOL LVL | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-48-50-01 | PID | 4 | OEM
|  | SS-4805A | SS | 4805 | 4805A | L4 REFRIGERATED PRECOOL SPEED SWTCH | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-48-50-01 | Equipment - Vendor Supplied Items | 4 | OEM
|  | XV-4805A | XV | 4805 | 4805A | L4 REFRIGERATED PRECOOL VLV | OEM | OEM | OEM | Others | [8 empty] | GFP-F-48-50-01 | PID | 4 | OEM
|  | ZS-4805A | ZS | 4805 | 4805A | L4 REFRIGERATED PRECOOL POS | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-48-50-01 | Equipment - Vendor Supplied Items | 4 | OEM
|  | ZS-4805B | ZS | 4805 | 4805B | L4 REFRIGERATED PRECOOL POS | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-48-50-01 | Equipment - Vendor Supplied Items | 4 | OEM
|  | ZS-4805C | ZS | 4805 | 4805C | L4 REFRIGERATED PRECOOL POS | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-48-50-01 | Equipment - Vendor Supplied Items | 4 | OEM
|  | TIT-4806A | TIT | 4806 | 4806A | L4 FREEZE TUNNEL FAN-01 TEMP | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-48-50-01 | PID | 4 | OEM
|  | WE-4010A | WE | 4010 | 4010A | L4 PEELER B ROTARY FD HPPR WEIGHT SENSOR | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-40-50-01 | Equipment - Vendor Supplied Items | 4 | OEM
|  | WE-4010B | WE | 4010 | 4010B | L4 PEELER B ROTARY FD HPPR WEIGHT SENSOR | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-40-50-01 | Equipment - Vendor Supplied Items | 4 | OEM
|  | WE-4010C | WE | 4010 | 4010C | L4 PEELER B ROTARY FD HPPR WEIGHT SENSOR | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-40-50-01 | Equipment - Vendor Supplied Items | 4 | OEM
|  | WIT-4010A | WIT | 4010 | 4010A | L4 PEELER B ROTARY FD HPPR WEIGHT | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-40-50-01 | PID | 4 | OEM
|  | LC-4011A | LC | 4011 | 4011A | L4 PEELER B LVL CNTRL | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-40-50-01 | PID | 4 | OEM
|  | LC-4011B | LC | 4011 | 4011B | L4 PEELER B LVL CNTRL | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-40-50-01 | PID | 4 | OEM
|  | LC-4011C | LC | 4011 | 4011C | L4 PEELER B LVL CNTRL | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-40-50-01 | PID | 4 | OEM
|  | PIT-4011A | PIT | 4011 | 4011A | L4 PEELER B PRESS | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-40-50-01 | Equipment - Vendor Supplied Items | 4 | OEM
|  | SV-4011A | SV | 4011 | 4011A | L4 PEELER B AIR VLV | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-40-50-01 | Equipment - Vendor Supplied Items | 4 | OEM
|  | XV-4011A | XV | 4011 | 4011A | L4 PEELER B STEAM VLV | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-40-50-01 | PID | 4 | OEM
|  | SV-4012A | SV | 4012 | 4012A | L4 PEELER B EXHST VESSEL COLD WTR VLV | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-40-50-01 | Equipment - Vendor Supplied Items | 4 | OEM
|  | XV-4012A | XV | 4012 | 4012A | L4 PEELER B EXHST VESSEL STEAM VLV | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-40-50-01 | Equipment - Vendor Supplied Items | 4 | OEM
|  | XV-4015A | XV | 4015 | 4015A | L4 PEELER B DISCH AUGER HOT WTR VLV | OEM | OEM | OEM | Others | [8 empty] | GFP-F-40-50-01 | PID | 4 | OEM
|  | AE-4087A | AE | 4087 | 4087A | L4 PEF ANALYSIS SENSOR | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-40-50-02-New | Equipment - Vendor Supplied Items | 4 | OEM
|  | AIT-4087A | AIT | 4087 | 4087A | L4 PEF ANALYSIS | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-40-50-02-New | PID | 4 | OEM
|  | LT-4087A | LT | 4087 | 4087A | L4 PEF LVL TRANSMITTER | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-40-50-02-New | Equipment - Vendor Supplied Items | 4 | OEM
|  | TE-4087A | TE | 4087 | 4087A | L4 PEF TEMP | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-40-50-02-New | Equipment - Vendor Supplied Items | 4 | OEM
|  | TT-4087A | TT | 4087 | 4087A | L4 PEF TEMP | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-40-50-02-New | PID | 4 | OEM
|  | XV-4087A | XV | 4087 | 4087A | L4 PEF COLD WTR VLV | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-40-50-02-New | PID | 4 | OEM
|  | XV-4087B | XV | 4087 | 4087B | L4 PEF HOT WTR VLV | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-40-50-02-New | PID | 4 | OEM
|  | XV-4087C | XV | 4087 | 4087C | L4 PEF DRN VLV | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-40-50-02-New | PID | 4 | OEM
|  | TT-4806A | TT | 4806 | 4806A | L4 FREEZE TUNNEL FAN-01 TEMP | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-48-50-01 | Equipment - Vendor Supplied Items | 4 | OEM
|  | TT-4806B | TT | 4806 | 4806B | L4 FREEZE TUNNEL AMMONIA TEMP | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-48-50-01 | Equipment - Vendor Supplied Items | 4 | OEM
|  | XV-4806A | XV | 4806 | 4806A | L4 FREEZE TUNNEL FAN-01 VLV | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-48-50-01 | Equipment - Vendor Supplied Items | 4 | OEM
|  | XV-4806B | XV | 4806 | 4806B | L4 FREEZE TUNNEL FAN-01 VLV | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-48-50-01 | Equipment - Vendor Supplied Items | 4 | OEM
|  | TIT-4807A | TIT | 4807 | 4807A | L4 FREEZE TUNNEL FAN-02 TEMP | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-48-50-01 | PID | 4 | OEM
|  | TT-4807A | TT | 4807 | 4807A | L4 FREEZE TUNNEL FAN-02 TEMP | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-48-50-01 | Equipment - Vendor Supplied Items | 4 | OEM
|  | XV-4807A | XV | 4807 | 4807A | L4 FREEZE TUNNEL FAN-02 VLV | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-48-50-01 | Equipment - Vendor Supplied Items | 4 | OEM
|  | XV-4807B | XV | 4807 | 4807B | L4 FREEZE TUNNEL FAN-02 VLV | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-48-50-01 | Equipment - Vendor Supplied Items | 4 | OEM
|  | TIT-4808A | TIT | 4808 | 4808A | L4 FREEZE TUNNEL FAN-03 TEMP | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-48-50-01 | PID | 4 | OEM
|  | TT-4808A | TT | 4808 | 4808A | L4 FREEZE TUNNEL FAN-03 TEMP | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-48-50-01 | Equipment - Vendor Supplied Items | 4 | OEM
|  | TT-4808B | TT | 4808 | 4808B | L4 FREEZE TUNNEL AMMONIA TEMP | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-48-50-01 | Equipment - Vendor Supplied Items | 4 | OEM
|  | XV-4808A | XV | 4808 | 4808A | L4 FREEZE TUNNEL FAN-03 VLV | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-48-50-01 | Equipment - Vendor Supplied Items | 4 | OEM
|  | XV-4808B | XV | 4808 | 4808B | L4 FREEZE TUNNEL FAN-03 VLV | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-48-50-01 | Equipment - Vendor Supplied Items | 4 | OEM
|  | TIT-4809A | TIT | 4809 | 4809A | L4 FREEZE TUNNEL FAN-04 TEMP | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-48-50-01 | PID | 4 | OEM
|  | TT-4809A | TT | 4809 | 4809A | L4 FREEZE TUNNEL FAN-04 TEMP | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-48-50-01 | Equipment - Vendor Supplied Items | 4 | OEM
|  | XV-4809A | XV | 4809 | 4809A | L4 FREEZE TUNNEL FAN-04 VLV | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-48-50-01 | Equipment - Vendor Supplied Items | 4 | OEM
|  | XV-4809B | XV | 4809 | 4809B | L4 FREEZE TUNNEL FAN-04 VLV | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-48-50-01 |  | 4 | OEM
|  | LS-4820A | LS | 4820 | 4820A | L4 PRECOOL CIP TROUGH LVL | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-48-50-01 | Equipment - Vendor Supplied Items | 4 | OEM
|  | LS-4820B | LS | 4820 | 4820B | L4 PRECOOL CIP TROUGH LVL | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-48-50-01 | Equipment - Vendor Supplied Items | 4 | OEM
|  | XV-4820A | XV | 4820 | 4820A | L4 PRECOOL CIP TROUGH VLV | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-48-50-01 | Equipment - Vendor Supplied Items | 4 | OEM
|  | XV-4820B | XV | 4820 | 4820B | L4 PRECOOL CIP TROUGH VLV | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-48-50-01 | PID | 4 | OEM
|  | XV-4821A | XV | 4821 | 4821A | L4 PRECOOL CIP RETURN PMP VLV | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-48-50-01 | PID | 4 | OEM
|  | XV-4821B | XV | 4821 | 4821B | L4 PRECOOL CIP RETURN PMP VLV | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-48-50-01 | PID | 4 | OEM
|  | SS-4825A | SS | 4825 | 4825A | L4 FREEZE TUNNEL SPEED | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-48-50-02 |  | 4 | OEM
|  | HC-9500A | HC | 9500 | 9500A | WESP HEAT CNTRL | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-95-50-02 | Equipment - Vendor Supplied Items | 4 | OEM
|  | HC-9500B | HC | 9500 | 9500B | WESP HEAT CNTRL | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-95-50-02 | Equipment - Vendor Supplied Items | 4 | OEM
|  | HC-9500C | HC | 9500 | 9500C | WESP HEAT CNTRL | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-95-50-02 | Equipment - Vendor Supplied Items | 4 | OEM
|  | HC-9500D | HC | 9500 | 9500D | WESP HEAT CNTRL | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-95-50-02 | Equipment - Vendor Supplied Items | 4 | OEM
|  | PI-9500A | PI | 9500 | 9500A | WESP PRESS | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-95-50-02 | Equipment - Vendor Supplied Items | 4 | OEM
|  | PT-9500A | PT | 9500 | 9500A | WESP PRESS TRANSMITTER | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-95-50-02 | PID | 4 | OEM
|  | TE-9500A | TE | 9500 | 9500A | WESP TEMP | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-95-50-02 | Equipment - Vendor Supplied Items | 4 | OEM
|  | TIT-9500A | TIT | 9500 | 9500A | WESP TEMP | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-95-50-02 | PID | 4 | OEM
|  | LA-9504A | LA | 9504 | 9504A | WESP LVL ALRM | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-95-50-02 | PID | 4 | OEM
|  | LT-9504A | LT | 9504 | 9504A | WESP LVL TRANSMITTER | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-95-50-02 | Equipment - Vendor Supplied Items | 4 | OEM
|  | PCV-9504A | PCV | 9504 | 9504A | WESP PRESS CNTRL VLV | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-95-50-02 | Equipment - Vendor Supplied Items | 4 | OEM
|  | PT-9504A | PT | 9504 | 9504A | WESP PRESS TRANSMITTER | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-95-50-02 | PID | 4 | OEM
|  | XV-9504A | XV | 9504 | 9504A | WESP VLV | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-95-50-02 | PID | 4 | OEM
|  | FE-9505A | FE | 9505 | 9505A | WESP FLOW SENSOR | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-95-50-02 | PID | 4 | OEM
|  | PI-9505A | PI | 9505 | 9505A | WESP PRESS | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-95-50-02 | Equipment - Vendor Supplied Items | 4 | OEM
|  | PT-9505A | PT | 9505 | 9505A | WESP PRESS TRANSMITTER | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-95-50-02 | PID | 4 | OEM
|  | XV-9505A | XV | 9505 | 9505A | WESP VLV | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-95-50-02 | PID | 4 | OEM
|  | LT-9506A | LT | 9506 | 9506A | WESP LVL TRANSMITTER | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-95-50-03 | Equipment - Vendor Supplied Items | 4 | OEM
|  | PCV-9506A | PCV | 9506 | 9506A | WESP PRESS CNTRL VLV | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-95-50-03 | Equipment - Vendor Supplied Items | 4 | OEM
|  | TE-9506A | TE | 9506 | 9506A | WESP TEMP | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-95-50-03 | PID | 4 | OEM
|  | XV-9506A | XV | 9506 | 9506A | WESP VLV | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-95-50-03 | PID | 4 | OEM
|  | PI-9507A | PI | 9507 | 9507A | WESP PRESS | OEM | OEM | OEM | OEM | [8 empty] | GFP-F-95-50-03 | Equipment - Vendor Supplied Items | 4 | OEM
|  | WE-4915A | WE | 4915 | 4915A | L4 FROZEN GRADING FD WEIGHT SENSOR | LOADCELL CABLE | Loadcell | SummingBox | OEM | [8 empty] | GFP-F-49-50-01 | PID | 4
|  | WE-4915B | WE | 4915 | 4915B | L4 FROZEN GRADING FD WEIGHT SENSOR | LOADCELL CABLE | Loadcell | SummingBox | OEM | [8 empty] | GFP-F-49-50-01 | PID | 4
|  | WE-4915C | WE | 4915 | 4915C | L4 FROZEN GRADING FD WEIGHT SENSOR | LOADCELL CABLE | Loadcell | SummingBox | OEM | [8 empty] | GFP-F-49-50-01 | PID | 4
|  | WE-4915D | WE | 4915 | 4915D | L4 FROZEN GRADING FD WEIGHT SENSOR | LOADCELL CABLE | Loadcell | SummingBox | OEM | [8 empty] | GFP-F-49-50-01 | PID | 4
|  | WE-4655A | WE | 4655 | 4655A | L4 BTTR WEIGH HPPR WEIGHT SENSOR | LOADCELL CABLE | Loadcell | SummingBox | OEM | [8 empty] | GFP-F-46-50-03 | Equipment - Vendor Supplied Items | 4
|  | WE-4655B | WE | 4655 | 4655B | L4 BTTR WEIGH HPPR WEIGHT SENSOR | LOADCELL CABLE | Loadcell | SummingBox | OEM | [8 empty] | GFP-F-46-50-03 | Equipment - Vendor Supplied Items | 4
|  | WE-4655C | WE | 4655 | 4655C | L4 BTTR WEIGH HPPR WEIGHT SENSOR | LOADCELL CABLE | Loadcell | SummingBox | OEM | [8 empty] | GFP-F-46-50-03 | Equipment - Vendor Supplied Items | 4
|  | WE-4660A | WE | 4660 | 4660A | L4 BTTR MIX TNK WEIGHT SENSOR | LOADCELL CABLE | Loadcell | SummingBox | OEM | [8 empty] | GFP-F-46-50-03 | Equipment - Vendor Supplied Items | 4
|  | WE-4660B | WE | 4660 | 4660B | L4 BTTR MIX TNK WEIGHT SENSOR | LOADCELL CABLE | Loadcell | SummingBox | OEM | [8 empty] | GFP-F-46-50-03 | Equipment - Vendor Supplied Items | 4
|  | WE-4660C | WE | 4660 | 4660C | L4 BTTR MIX TNK WEIGHT SENSOR | LOADCELL CABLE | Loadcell | SummingBox | OEM | [8 empty] | GFP-F-46-50-03 | Equipment - Vendor Supplied Items | 4

## ASi
Device | ASi Master | ASi Trunk | ASi Node | ASi Module | DI1 | DI2 | DI3 | DI4 | DO1 | DO2 | DO3 | DO4 | AI1 | AI2 | AI3 | AI4 | AO1 | AO2 | AO3 | AO4
L04PRC-R1-JB02-AM01 | L04PRC-R1-ASM01 | 0 | 1 | L04PRC-R1-JB01-AM01 | DO1: XV-4082A
L04PRC-R1-JB03-AM01 | L04PRC-R1-ASM01 | 0 | 2 | L04PRC-R1-JB02-AM01 | AI1: LIT-4084A
L04PRC-R1-JB04-AM01 | L04PRC-R1-ASM01 | 0 | 3 | L04PRC-R1-JB02-AM02 | DI1: FS-4090A; DO1: SV-5677A
L04PRC-R1-JB05-AM01 | L04PRC-R1-ASM01 | 0 | 4 | L04PRC-R1-JB03-AM01 | AI1: LIT-4460A
L04PRC-R1-JB05-AM02 | L04PRC-R1-ASM01 | 0 | 5 | L04PRC-R1-JB04-AM01 | AI1: LIT-4505A
L04PRC-R1-JB06-AM01 | L04PRC-R1-ASM01 | 0 | 6 | L04PRC-R1-JB05-AM01 | AI1: TT-4505A; AI2: TT-4505C; AI3: LIT-4530A; AI4: TT-4535A
L04PRC-R1-JB06-AM02 | L04PRC-R1-ASM01 | 0 | 7 | L04PRC-R1-JB05-AM02 | AI1: TT-4535C
L04PRC-R1-JB07-AM01 | L04PRC-R1-ASM01 | 0 | 8 | L04PRC-R1-JB05-AM03 | DI1: LSL-4505A; DI2: ZS-4505A; DI3: ZS-4505B; DI4: LSL-4535A
L04PRC-R1-JB02-AM02 | L04PRC-R1-ASM01 | 0 | 9A | L04PRC-R1-JB05-AM04 | DI1: ZS-4535B; DI2: ZS-4535G; DO1: SV-4505B; DO2: SV-4535B
L04PRC-R1-JB05-AM03 | L04PRC-R1-ASM01 | 0 | 9B | L04PRC-R1-JB06-AM01 | AI1: TT-4505B; AI2: TT-4505D; AI3: HIT-4518A; AI4: HIT-4528A
L04PRC-R1-JB05-AM04 | L04PRC-R1-ASM01 | 0 | 10A | L04PRC-R1-JB06-AM02 | AI1: TT-4535B; AI2: TT-4535D; AI3: HIT-4548A; AI4: HIT-4558A
L04PRC-R1-JB06-AM03 | L04PRC-R1-ASM01 | 0 | 10B | L04PRC-R1-JB06-AM03 | DI1: TSH-4505A; DI2: TSH-4505B; DI3: PSL-4510A; DI4: PSL-4518A
L04PRC-R1-JB06-AM04 | L04PRC-R1-ASM01 | 0 | 11A | L04PRC-R1-JB06-AM04 | DI1: TSH-4518A; DI2: PSL-4520A; DI3: PSL-4528A; DI4: TSH-4528A
L04PRC-R1-JB06-AM05 | L04PRC-R1-ASM01 | 0 | 11B | L04PRC-R1-JB06-AM05 | DI1: TSH-4535A; DI2: TSH-4535B; DI3: PSL-4540A; DI4: PSL-4548A
L04PRC-R1-JB06-AM06 | L04PRC-R1-ASM01 | 0 | 12A | L04PRC-R1-JB06-AM06 | DI1: TSH-4548A; DI2: PSL-4550A; DI3: PSL-4558A; DI4: TSH-4558A
L04PRC-R1-JB07-AM02 | L04PRC-R1-ASM01 | 0 | 12B | L04PRC-R1-JB07-AM01 | AI1: LIT-4568A; AI2: TT-7480B; AI3: PT-7481B; AI4: PT-7481A
L04PRC-R1-JB01-AM01 | L04PRC-R1-ASM01 | 0 | 13A | L04PRC-R1-JB07-AM02 | DI1: FS-7480A
L04PRC-R1-JB08-AM01 | L04PRC-R1-ASM01 | 0 | 13B | L04PRC-R1-JB08-AM01 | DO1: SV-4568A
XV-4084A | L04PRC-R1-ASM01 | 1 | 1A | L04PRC-R2-JB01-AM01 | AI1: FIT-4670A; AI2: PIT-4670A; AI3: TIT-4670A; AI4: TIT-4670B
XV-4084B | L04PRC-R1-ASM01 | 1 | 1B | L04PRC-R2-JB01-AM02 | AI1: LIT-4686A; AI2: TT-4686A; AI3: LIT-4692A; AI4: LIT-4723A
XV-4090A | L04PRC-R1-ASM01 | 1 | 2A | L04PRC-R2-JB01-AM03 | AI1: LIT-4665A; AI2: TT-4665A; AI3: TCV-4670A; AI4: LV-4686A
XV-4460A | L04PRC-R1-ASM01 | 1 | 2B | L04PRC-R2-JB01-AM04 | AO1: TCV-4670A; AO2: LV-4686A
XV-4505A | L04PRC-R1-ASM01 | 1 | 3A | L04PRC-R2-JB01-AM05 | DI1: ZS-4665A; DI2: LSH-4723A; DO1: SV-4667A; DO2: SV-4693E
XV-4505B | L04PRC-R1-ASM01 | 1 | 3B | L04PRC-R2-JB02-AM01 | DI1: HSB-4681A; DI2: HSF-4681A; DI3: ZSB-4681A; DI4: ZSF-4681A
XV-4506A | L04PRC-R1-ASM01 | 1 | 4A | L04PRC-R2-JB02-AM02 | DI1: HSD-4685A; DI2: HSU-4685A; DI3: SS-4685B; DI4: ZSH-4685A
XV-4506B | L04PRC-R1-ASM01 | 1 | 4B | L04PRC-R2-JB02-AM03 | DI1: ZSL-4685A
XV-4535A | L04PRC-R1-ASM01 | 1 | 5A | L04PRC-R2-JB03-AM01 | DI1: SS-4685A; DI2: HSB-4690A; DI3: HSF-4690A; DI4: ZSB-4690A
XV-4535B | L04PRC-R1-ASM01 | 1 | 5B | L04PRC-R2-JB03-AM02 | DI1: ZSF-4690A
XV-4536A | L04PRC-R1-ASM01 | 1 | 6A | L04PRC-R3-JB01-AM01 | DI1: ZSD-4706A; DI2: ZSU-4706B; DO1: SV-4705A
XV-4536B | L04PRC-R1-ASM01 | 1 | 6B | L04PRC-R3-JB02-AM01 | AI1: FIT-4705A; AI2: LIT-4705A; AI3: LIT-4711A; AI4: PIT-4783A
XV-4565A | L04PRC-R1-ASM01 | 1 | 7A | L04PRC-R3-JB02-AM02 | AI1: TT-4783A; AI2: PIT-4783B; AI3: FV-4705A; AI4: FV-4705B
L04PRC-R2-JB01-AM01 | L04PRC-R2-ASM01 | 0 | 1 | L04PRC-R3-JB02-AM03 | AO1: FV-4705A; AO2: FV-4705B; AO3: FV-4705C; AO4: FV-4705D
L04PRC-R2-JB01-AM02 | L04PRC-R2-ASM01 | 0 | 2 | L04PRC-R3-JB02-AM04 | AI1: FV-4705C; AI2: FV-4705D; AI3: FV-4705E; AI4: FV-4705F
L04PRC-R2-JB01-AM03 | L04PRC-R2-ASM01 | 0 | 3 | L04PRC-R3-JB02-AM05 | AO1: FV-4705E; AO2: FV-4705F
L04PRC-R2-JB01-AM05 | L04PRC-R2-ASM01 | 0 | 4A | L04PRC-R3-JB02-AM06 | DI1: LSH-4705A; DI2: HSD-4706A; DI3: HSU-4706B; DI4: LSH-4711A
L04PRC-R2-JB02-AM01 | L04PRC-R2-ASM01 | 0 | 4B | L04PRC-R3-JB03-AM01 | AI1: LIT-4718A; AI2: PIT-4730A; AI3: PIT-4730B; AI4: TT-4730A
L04PRC-R2-JB02-AM02 | L04PRC-R2-ASM01 | 0 | 5A | L04PRC-R3-JB03-AM02 | AI1: FIT-4732A; AI2: LIT-4732A; AI3: PIT-4732A; AI4: PIT-4732B
L04PRC-R2-JB02-AM03 | L04PRC-R2-ASM01 | 0 | 5B | L04PRC-R3-JB03-AM03 | AI1: TT-4732A; AI2: LIT-4735A; AI3: FV-4732A; AI4: LCV-4732A
L04PRC-R2-JB03-AM01 | L04PRC-R2-ASM01 | 0 | 6A | L04PRC-R3-JB03-AM04 | AO1: FV-4732A; AO2: LCV-4732A; AO3: TCV-4732A
L04PRC-R2-JB01-AM04 | L04PRC-R2-ASM01 | 0 | 16 | L04PRC-R3-JB03-AM05 | AI1: TCV-4732A
XV-4666A | L04PRC-R2-ASM01 | 1 | 1A | L04PRC-R3-JB03-AM06 | DI1: ZSS-4717A; DI2: FS-4718A; DI3: ZSS-4719A; DI4: LSH-4735A; DO1: SV-4718A; DO2: SV-4720A
XV-4670C | L04PRC-R2-ASM01 | 1 | 1B | L04PRC-R3-JB04-AM01 | AI1: TT-4705A; AI2: TT-4705B; AI3: TT-4705C; AI4: LCV-4715A
XV-4670D | L04PRC-R2-ASM01 | 1 | 2A | L04PRC-R3-JB04-AM02 | AO1: LCV-4715A
XV-4665B | L04PRC-R2-ASM01 | 1 | 2B | L04PRC-R3-JB04-AM03 | DI1: ZS-4715A; DO1: SV-4716A
XV-4665D | L04PRC-R2-ASM01 | 1 | 3A | L04PRC-R4-JB01-AM01 | AO1: LCV-4745A
XV-4665E | L04PRC-R2-ASM01 | 1 | 3B | L04PRC-R4-JB01-AM02 | AI1: LCV-4745A
XV-4685B | L04PRC-R2-ASM01 | 1 | 4A | L04PRC-R4-JB01-AM03 | DI1: ZS-4745A; DI2: SS-4755A; DI3: SS-4757A; DO1: SV-4746A
XV-4685C | L04PRC-R2-ASM01 | 1 | 4B | L04PRC-R2-JB09-AM01 | AI1: LIT-4710A; AI2: TT-4710A; AI3: TT-4710B; AI4: TT-4710C
XV-4692B | L04PRC-R2-ASM01 | 1 | 5A | L04PRC-R2-JB09-AM02 | AI1: TT-4710D
XV-4693A | L04PRC-R2-ASM01 | 1 | 5B | L04PRC-R4-JB03-AM01 | AO1: FV-4710A; AO2: FV-4710B; AO3: FV-4710C; AO4: FV-4710D
XV-4693B | L04PRC-R2-ASM01 | 1 | 6A | L04PRC-R4-JB03-AM02 | AI1: FV-4710A; AI2: FV-4710B; AI3: FV-4710C; AI4: FV-4710D
XV-4693C | L04PRC-R2-ASM01 | 1 | 6B | L04PRC-R4-JB03-AM03 | AO1: FV-4710E; AO2: FV-4710F; AO3: FV-4710G; AO4: FV-4710H
XV-4693D | L04PRC-R2-ASM01 | 1 | 7A | L04PRC-R4-JB03-AM04 | AI1: FV-4710E; AI2: FV-4710F; AI3: FV-4710G; AI4: FV-4710H
XV-4693E | L04PRC-R2-ASM01 | 1 | 7B | L04PRC-R4-JB03-AM05 | DI1: LSH-4710A
XV-4693F | L04PRC-R2-ASM01 | 1 | 8A | L04PRC-R4-JB04-AM01 | DI1: HSD-4707A; DI2: HSU-4707B; DI3: SS-4707A; DI4: SS-4707B
XV-4693G | L04PRC-R2-ASM01 | 1 | 8B | L04PRC-R4-JB04-AM02 | DI1: ZSD-4707A; DI2: ZSU-4707B
XV-4693H | L04PRC-R2-ASM01 | 1 | 9A | L04PRC-R4-JB05-AM01 | AI1: LIT-4748A; AI2: PIT-4765A; AI3: PIT-4765B; AI4: TT-4765A
XV-4693J | L04PRC-R2-ASM01 | 1 | 9B | L04PRC-R4-JB05-AM02 | AI1: FIT-4767A; AI2: LIT-4767A; AI3: PIT-4767A; AI4: PIT-4767B
XV-4693K | L04PRC-R2-ASM01 | 1 | 10A | L04PRC-R4-JB05-AM03 | AI1: TT-4767A; AI2: LIT-4770A; AI3: FV-4767A; AI4: TCV-4767A
XV-4693L | L04PRC-R2-ASM01 | 1 | 10B | L04PRC-R4-JB05-AM04 | AO1: FV-4767A; AO2: TCV-4767A
XV-4695A | L04PRC-R2-ASM01 | 1 | 11A | L04PRC-R4-JB05-AM05 | DI1: ZSS-4747A; DI2: FS-4748A; DI3: ZSS-4749A; DI4: LSH-4770A; DO1: SV-4748A; DO2: SV-4750A
XV-4723A | L04PRC-R2-ASM01 | 1 | 11B | L04PRC-R4-JB06-AM01 | AI1: LIT-4791A; AI2: LIT-4792A
XV-4723C | L04PRC-R2-ASM01 | 1 | 12A | L04PRC-R4-JB06-AM02 | DI1: ZSS-4785A; DI2: ZSS-4785B; DI3: ZSS-4785C; DI4: ZSS-4785D
XV-4726B | L04PRC-R2-ASM01 | 1 | 12B | L04PRC-R4-JB06-AM03 | DI1: ZSS-4785E; DI2: ZSS-4785F; DI3: ZSS-4785G; DI4: ZSS-4785H
XV-4726C | L04PRC-R2-ASM01 | 1 | 13A | L04PRC-R4-JB06-AM04 | DI1: ZSS-4785J; DI2: ZSS-4785K; DI3: ZSS-4785L; DI4: ZSS-4785M
L04PRC-R3-JB02-AM01 | L04PRC-R3-ASM01 | 0 | 1 | L04PRC-R4-JB06-AM05 | DI1: ZSS-4785N; DI2: LSH-4791A
L04PRC-R3-JB02-AM02 | L04PRC-R3-ASM01 | 0 | 2 | L04PRC-R5-JB01-AM01 | AI1: TT-4605B; AI2: PIT-4610A; AI3: PIT-4610B; AI4: TT-4610B
L04PRC-R3-JB03-AM01 | L04PRC-R3-ASM01 | 0 | 3 | L04PRC-R5-JB01-AM02 | AI1: TT-4610C
L04PRC-R3-JB03-AM02 | L04PRC-R3-ASM01 | 0 | 4 | L04PRC-R5-JB01-AM03 | DI1: FS-4611A
L04PRC-R3-JB03-AM03 | L04PRC-R3-ASM01 | 0 | 5 | L04PRC-R5-JB02-AM01 | AI1: LIT-4616A; AI2: TT-4616B; AI3: TT-4619A
L04PRC-R3-JB04-AM01 | L04PRC-R3-ASM01 | 0 | 6 | L04PRC-R5-JB02-AM02 | DI1: ZS-4615A; DI2: ZS-4615B; DI3: ZSS-4628A; DI4: LSH-4629A; DO1: SV-4617A; DO2: SV-4628A; DO3: SV-4632A
L04PRC-R3-JB02-AM04 | L04PRC-R3-ASM01 | 0 | 7 | L04PRC-R5-JB02-AM03 | DI1: LSL-4629B
L04PRC-R3-JB03-AM05 | L04PRC-R3-ASM01 | 0 | 8 | L04PRC-R5-JB03-AM01 | AI1: FIT-4660A; AI2: TT-4660A
L04PRC-R3-JB01-AM01 | L04PRC-R3-ASM01 | 0 | 9A | L04PRC-R5-JB03-AM02 | DO1: SV-4655A; DO2: SV-4656B; DO3: SV-4663A; DO4: SV-4664A
L04PRC-R3-JB03-AM06 | L04PRC-R3-ASM01 | 0 | 9B | L04PRC-R6-JB01-AM01 | AI1: LIT-4910C; AI2: LIT-4910E
L04PRC-R3-JB04-AM03 | L04PRC-R3-ASM01 | 0 | 10A | L04PRC-R6-JB01-AM02 | DI1: ZS-4910D; DI2: ZS-4910F; DO1: XV-4910A; DO2: XV-4910B
L04PRC-R2-JB03-AM02 | L04PRC-R3-ASM01 | 0 | 10B | L04PRC-R6-JB02-AM01 | AI1: LIT-4912A; AI2: LIT-4912C
L04PRC-R3-JB02-AM06 | L04PRC-R3-ASM01 | 0 | 11A | L04PRC-R6-JB02-AM02 | DI1: ZS-4912B; DI2: ZS-4912D; DO1: XV-4912A
L04PRC-R3-JB02-AM03 | L04PRC-R3-ASM01 | 0 | 16 | L04PRC-R6-JB04-AM01 | AI1: LIT-4860A
L04PRC-R3-JB02-AM05 | L04PRC-R3-ASM01 | 0 | 17
L04PRC-R3-JB03-AM04 | L04PRC-R3-ASM01 | 0 | 18
L04PRC-R3-JB04-AM02 | L04PRC-R3-ASM01 | 0 | 19
XV-4689A | L04PRC-R3-ASM01 | 1 | 1A
XV-4705A | L04PRC-R3-ASM01 | 1 | 1B
XV-4705B | L04PRC-R3-ASM01 | 1 | 2A
XV-4711A | L04PRC-R3-ASM01 | 1 | 2B
XV-4713A | L04PRC-R3-ASM01 | 1 | 3A
XV-4714A | L04PRC-R3-ASM01 | 1 | 3B
XV-4715A | L04PRC-R3-ASM01 | 1 | 4A
XV-4717A | L04PRC-R3-ASM01 | 1 | 4B
XV-4718A | L04PRC-R3-ASM01 | 1 | 5A
XV-4718B | L04PRC-R3-ASM01 | 1 | 5B
XV-4719A | L04PRC-R3-ASM01 | 1 | 6A
XV-4722A | L04PRC-R3-ASM01 | 1 | 6B
XV-4722B | L04PRC-R3-ASM01 | 1 | 7A
XV-4722C | L04PRC-R3-ASM01 | 1 | 7B
XV-4722D | L04PRC-R3-ASM01 | 1 | 8A
XV-4725A | L04PRC-R3-ASM01 | 1 | 8B
XV-4725B | L04PRC-R3-ASM01 | 1 | 9A
XV-4728A | L04PRC-R3-ASM01 | 1 | 9B
XV-4728B | L04PRC-R3-ASM01 | 1 | 10A
XV-4728C | L04PRC-R3-ASM01 | 1 | 10B
XV-4728D | L04PRC-R3-ASM01 | 1 | 11A
XV-4730A | L04PRC-R3-ASM01 | 1 | 11B
XV-4730B | L04PRC-R3-ASM01 | 1 | 12A
XV-4730C | L04PRC-R3-ASM01 | 1 | 12B
XV-4730D | L04PRC-R3-ASM01 | 1 | 13A
XV-4730E | L04PRC-R3-ASM01 | 1 | 13B
XV-4732A | L04PRC-R3-ASM01 | 1 | 14A
XV-4732B | L04PRC-R3-ASM01 | 1 | 14B
XV-4732C | L04PRC-R3-ASM01 | 1 | 15A
XV-4735A | L04PRC-R3-ASM01 | 1 | 15B
XV-4736A | L04PRC-R3-ASM01 | 1 | 16A
XV-4738D | L04PRC-R3-ASM01 | 1 | 16B
XV-4738E | L04PRC-R3-ASM01 | 1 | 17A
XV-4739C | L04PRC-R3-ASM01 | 1 | 17B
XV-4739D | L04PRC-R3-ASM01 | 1 | 18A
L04PRC-R2-JB09-AM01 | L04PRC-R4-ASM01 | 0 | 1
L04PRC-R2-JB09-AM02 | L04PRC-R4-ASM01 | 0 | 2
L04PRC-R4-JB05-AM01 | L04PRC-R4-ASM01 | 0 | 3
L04PRC-R4-JB05-AM02 | L04PRC-R4-ASM01 | 0 | 4
L04PRC-R4-JB05-AM03 | L04PRC-R4-ASM01 | 0 | 5
L04PRC-R4-JB06-AM01 | L04PRC-R4-ASM01 | 0 | 6
L04PRC-R4-JB01-AM02 | L04PRC-R4-ASM01 | 0 | 7
L04PRC-R4-JB03-AM02 | L04PRC-R4-ASM01 | 0 | 8
L04PRC-R4-JB03-AM04 | L04PRC-R4-ASM01 | 0 | 9
L04PRC-R4-JB01-AM03 | L04PRC-R4-ASM01 | 0 | 10A
L04PRC-R4-JB05-AM05 | L04PRC-R4-ASM01 | 0 | 10B
L04PRC-R4-JB03-AM05 | L04PRC-R4-ASM01 | 0 | 11A
L04PRC-R4-JB04-AM01 | L04PRC-R4-ASM01 | 0 | 11B
L04PRC-R4-JB04-AM02 | L04PRC-R4-ASM01 | 0 | 12A
L04PRC-R4-JB06-AM02 | L04PRC-R4-ASM01 | 0 | 12B
L04PRC-R4-JB06-AM03 | L04PRC-R4-ASM01 | 0 | 13A
L04PRC-R4-JB06-AM04 | L04PRC-R4-ASM01 | 0 | 13B
L04PRC-R4-JB06-AM05 | L04PRC-R4-ASM01 | 0 | 14A
L04PRC-R4-JB01-AM01 | L04PRC-R4-ASM01 | 0 | 16
L04PRC-R4-JB03-AM01 | L04PRC-R4-ASM01 | 0 | 17
L04PRC-R4-JB03-AM03 | L04PRC-R4-ASM01 | 0 | 18
L04PRC-R4-JB05-AM04 | L04PRC-R4-ASM01 | 0 | 19
XV-4710A | L04PRC-R4-ASM01 | 1 | 1A
XV-4745A | L04PRC-R4-ASM01 | 1 | 1B
XV-4747A | L04PRC-R4-ASM01 | 1 | 2A
XV-4748A | L04PRC-R4-ASM01 | 1 | 2B
XV-4748B | L04PRC-R4-ASM01 | 1 | 3A
XV-4749A | L04PRC-R4-ASM01 | 1 | 3B
XV-4753A | L04PRC-R4-ASM01 | 1 | 4A
XV-4753B | L04PRC-R4-ASM01 | 1 | 4B
XV-4753C | L04PRC-R4-ASM01 | 1 | 5A
XV-4757A | L04PRC-R4-ASM01 | 1 | 5B
XV-4759A | L04PRC-R4-ASM01 | 1 | 6A
XV-4759B | L04PRC-R4-ASM01 | 1 | 6B
XV-4765A | L04PRC-R4-ASM01 | 1 | 7A
XV-4765B | L04PRC-R4-ASM01 | 1 | 7B
XV-4765C | L04PRC-R4-ASM01 | 1 | 8A
XV-4765D | L04PRC-R4-ASM01 | 1 | 8B
XV-4765E | L04PRC-R4-ASM01 | 1 | 9A
XV-4765F | L04PRC-R4-ASM01 | 1 | 9B
XV-4765G | L04PRC-R4-ASM01 | 1 | 10A
XV-4765H | L04PRC-R4-ASM01 | 1 | 10B
XV-4765J | L04PRC-R4-ASM01 | 1 | 11A
XV-4767A | L04PRC-R4-ASM01 | 1 | 11B
XV-4767B | L04PRC-R4-ASM01 | 1 | 12A
XV-4767C | L04PRC-R4-ASM01 | 1 | 12B
XV-4770A | L04PRC-R4-ASM01 | 1 | 13A
XV-4771A | L04PRC-R4-ASM01 | 1 | 13B
XV-4773D | L04PRC-R4-ASM01 | 1 | 14A
XV-4773E | L04PRC-R4-ASM01 | 1 | 14B
XV-4785A | L04PRC-R4-ASM01 | 1 | 15A
XV-4785B | L04PRC-R4-ASM01 | 1 | 15B
XV-4785C | L04PRC-R4-ASM01 | 1 | 16A
XV-4785D | L04PRC-R4-ASM01 | 1 | 16B
XV-4785E | L04PRC-R4-ASM01 | 1 | 17A
XV-4785F | L04PRC-R4-ASM01 | 1 | 17B
XV-4786A | L04PRC-R4-ASM01 | 1 | 18A
XV-4786B | L04PRC-R4-ASM01 | 1 | 18B
XV-4786C | L04PRC-R4-ASM01 | 1 | 19A
XV-4786D | L04PRC-R4-ASM01 | 1 | 19B
XV-4786E | L04PRC-R4-ASM01 | 1 | 20A
XV-4791A | L04PRC-R4-ASM01 | 1 | 20B
XV-4792A | L04PRC-R4-ASM01 | 1 | 21A
XV-4793A | L04PRC-R4-ASM01 | 1 | 21B
XV-4793B | L04PRC-R4-ASM01 | 1 | 22A
XV-4794A | L04PRC-R4-ASM01 | 1 | 22B
XV-4794B | L04PRC-R4-ASM01 | 1 | 23A
L04PRC-R5-JB01-AM01 | L04PRC-R5-ASM01 | 0 | 1
L04PRC-R5-JB01-AM02 | L04PRC-R5-ASM01 | 0 | 2
L04PRC-R5-JB02-AM01 | L04PRC-R5-ASM01 | 0 | 3
L04PRC-R5-JB03-AM01 | L04PRC-R5-ASM01 | 0 | 4
L04PRC-R5-JB02-AM02 | L04PRC-R5-ASM01 | 0 | 5A
L04PRC-R5-JB03-AM02 | L04PRC-R5-ASM01 | 0 | 5B
L04PRC-R5-JB01-AM03 | L04PRC-R5-ASM01 | 0 | 6A
L04PRC-R5-JB02-AM03 | L04PRC-R5-ASM01 | 0 | 6B
XV-4610A | L04PRC-R5-ASM01 | 1 | 1A
XV-4616A | L04PRC-R5-ASM01 | 1 | 1B
XV-4616B | L04PRC-R5-ASM01 | 1 | 2A
XV-4616D | L04PRC-R5-ASM01 | 1 | 2B
XV-4619A | L04PRC-R5-ASM01 | 1 | 3A
XV-4619B | L04PRC-R5-ASM01 | 1 | 3B
XV-4659A | L04PRC-R5-ASM01 | 1 | 4A
XV-4660C | L04PRC-R5-ASM01 | 1 | 4B
XV-4660D | L04PRC-R5-ASM01 | 1 | 5A
XV-4660E | L04PRC-R5-ASM01 | 1 | 5B
XV-4660F | L04PRC-R5-ASM01 | 1 | 6A
XV-4660G | L04PRC-R5-ASM01 | 1 | 6B
XV-4662A | L04PRC-R5-ASM01 | 1 | 7A
L04PRC-R6-JB01-AM01 | L04PRC-R6-ASM01 | 0 | 1
L04PRC-R6-JB02-AM01 | L04PRC-R6-ASM01 | 0 | 2
L04PRC-R6-JB04-AM01 | L04PRC-R6-ASM01 | 0 | 3
L04PRC-R6-JB01-AM02 | L04PRC-R6-ASM01 | 0 | 4A
L04PRC-R6-JB02-AM02 | L04PRC-R6-ASM01 | 0 | 4B

## Panels
PLC Panels | Remote Panels | ASi Master 1 | ASi Master 2 | ASi Master 3 | JBs | Module 1 | Module 2 | Module 3 | Module 4 | Module 5 | Module 6 | Module 7 | Module 8 | Module | Count
L4_PRC | L04PRC-R1 | L04PRC-R1-ASM01 |  |  | L04PRC-R1-JB01 | AC2267 | [7 empty] | AC2216 | 35
| L04PRC-R2 | L04PRC-R2-ASM01 |  |  | L04PRC-R1-JB02 | AC2216 | AC2259 | [6 empty] | AC2218 | 9
| L04PRC-R3 | L04PRC-R3-ASM01 |  |  | L04PRC-R1-JB03 | AC2216 | [7 empty] | AC2259 | 9
| L04PRC-R4 | L04PRC-R4-ASM01 |  |  | L04PRC-R1-JB04 | AC2216 | [7 empty] | AC2267 | 26
| L04PRC-R5 | L04PRC-R5-ASM01 |  |  | L04PRC-R1-JB05 | AC2216 | AC2216 | AC2267 | AC2267
| L04PRC-R6 | L04PRC-R6-ASM01 |  |  | L04PRC-R1-JB06 | AC2216 | AC2216 | AC2267 | AC2267 | AC2267 | AC2267
[5 empty] | L04PRC-R1-JB07 | AC2216 | AC2267
[5 empty] | L04PRC-R1-JB08 | AC2267
[5 empty] | L04PRC-R2-JB01 | AC2216 | AC2216 | AC2216 | AC2218 | AC2259
[5 empty] | L04PRC-R2-JB02 | AC2267 | AC2267 | AC2267
[5 empty] | L04PRC-R2-JB03 | AC2267 | AC2267
[5 empty] | L04PRC-R3-JB01 | AC2259
[5 empty] | L04PRC-R3-JB02 | AC2216 | AC2216 | AC2218 | AC2216 | AC2218 | AC2267
[5 empty] | L04PRC-R3-JB03 | AC2216 | AC2216 | AC2216 | AC2218 | AC2216 | AC2259
[5 empty] | L04PRC-R3-JB04 | AC2216 | AC2218 | AC2259
[5 empty] | L04PRC-R4-JB01 | AC2218 | AC2216 | AC2259
[5 empty] | L04PRC-R2-JB09 | AC2216 | AC2216
[5 empty] | L04PRC-R4-JB03 | AC2218 | AC2216 | AC2218 | AC2216 | AC2267
[5 empty] | L04PRC-R4-JB04 | AC2267 | AC2267
[5 empty] | L04PRC-R4-JB05 | AC2216 | AC2216 | AC2216 | AC2218 | AC2259
[5 empty] | L04PRC-R4-JB06 | AC2216 | AC2267 | AC2267 | AC2267 | AC2267
[5 empty] | L04PRC-R5-JB01 | AC2216 | AC2216 | AC2267
[5 empty] | L04PRC-R5-JB02 | AC2216 | AC2259 | AC2267
[5 empty] | L04PRC-R5-JB03 | AC2216 | AC2259
[5 empty] | L04PRC-R6-JB01 | AC2216 | AC2267
[5 empty] | L04PRC-R6-JB02 | AC2216 | AC2267
L04PRC-R6-JB03
[5 empty] | L04PRC-R6-JB04 | AC2216